## Index
Abstract of schedule of rates for 2015-16 : Cost Data per Km of 33/11 KV/LT Lines
Sl. No | Particulars of items | Wind. pr.in kg/m2 | W. Load in kg. | Type of pole being used | No. of poles/KM | Span in Mtrs | Size of Conductor | Total Cost in Rs. | Page No
1 | 33KV line |  |  | 11.0Mtr. Spun | 18 | 60 | 100Sqmm AAA | 641609 | 15
2 | 33KV line |  |  | 12.5Mtr. Spun | 18 | 60 | 100Sqmm AAA | 686079 | 16
3 | 33KV line (Double Circuit) |  |  | 12.5Mtr. Spun | 18 | 60 | 100Sqmm AAA | 1021300 | 17
4 | 33 KV Line | 75 | 280 | 9.1 Mtr. PSCC | 27 | 40 | 100 Sqmm AAA | 548300 | 18
5 | 33 KV Line | 100 | 280 | 9.1 Mtr. PSCC | 19 | 60 | 100 Sqmm AAA | 462800 | 19
6 | 11 KV Line | 75 | 140 | 9.1 Mtr. PSCC | 27 | 40 | 100 Sqmm AAA | 464400 | 20
7 | 11 KV Line | 100 | 200 | 9.1 Mtr. PSCC | 18 | 60 | 55 Sqmm AAA | 308400 | 21
8 | 11 KV Line | 75 | 140 | 8.0 Mtr PSCC(140Kgs) | 22 | 50 | 55 Sqmm AAA | 274600 | 22
9 | 11 KV Line | 100 | 200 | 8.0 Mtr PSCC(200Kgs) | 22 | 50 | 55 Sqmm AAA | 278000 | 23
10 | 6.3 KV Line | 75 | 140 | 9.1 Mtr. PSCC | 21 | 50 | 55 Sqmm AAA | 260800 | 24
11 | 6.3 KV Line | 100 | 200 | 8.0 Mtr PSCC(140Kgs) | 18 | 60 | 55 Sqmm AAA | 188200 | 25
12 | L.T. 3Ph 5 Wire Line(Horizontal) | 75 | 140 | 8.0 Mtr PSCC (200Kgs) | 28 | 40 | 4x55+1x34 Sqmm AAA | 330500 | 26
13 | L.T. 3Ph 5 Wire Line(Horizontal) | 100 | 200 | 8.0 Mtr PSCC (200Kgs) | 21 | 50 | 3x55+2x34 Sqmm AAA | 284800 | 27
14 | L.T. 3Ph 5 Wire Line(Horizontal) | 75 | 140 | 8.0 Mtr PSCC (200Kgs) | 21 | 50 | 5x34 Sqmm AAA | 237700 | 28
15 | L.T. 3Ph 5 Wire Line(Horizontal) | 100 | 200 | 8.0 Mtr PSCC(140Kgs) | 28 | 40 | 4x55+1x34 Sqmm AAA | 326600 | 29
16 | L.T. 3Ph 5 Wire Line(Horizontal) | 75 | 140 | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 3x55+2x34 Sqmm AAA | 281800 | 30
17 | L.T. 3Ph 5 Wire Line(Horizontal) | 100 | 200 | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 5x34 Sqmm AAA | 235600 | 31
18 | L.T. 3Ph 4 Wire Line(Horizontal) | 75 | 140 | 8.0 Mtr PSCC(140Kgs) | 28 | 40 | 4x55 Sqmm AAA | 298500 | 32 | 580500
19 | L.T. 3Ph 4 Wire Line(Horizontal) | 100 | 200 | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 4x34 Sqmm AAA | 208400 | 33 | 413125
20 | L.T. 3Ph 4 Wire Line(Horizontal) | 75 | 140 | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 4x55 Sqmm AAA | 270000 | 34 | 287375
21 | L.T. 1Ph 3 Wire Line(Horizontal) | 75 | 140 | 8.0 Mtr PSCC(140Kgs) | 28 | 40 | 3x55 Sqmm AAA | 258100 | 35
22 | L.T. 1Ph 3 Wire Line(Horizontal) | 75 | 140 | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 3x34 Sqmm AAA | 183700 | 36
23 | L.T. 1Ph 3 Wire Line(Horizontal) |  |  | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 3x55 Sqmm AAA | 229900 | 37
24 | L.T. 1Ph 2 Wire Line(Horizontal) |  |  | 8.0 Mtr PSCC(140Kgs) | 28 | 40 | 2x55 Sqmm AAA | 210600 | 38
25 | L.T. 1Ph 2 Wire Line(Horizontal) |  |  | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 2x34 Sqmm AAA | 152700 | 39
26 | L.T. 1Ph 2 Wire Line(Horizontal) |  |  | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 2x55 Sqmm AAA | 183500 | 40
27 | L.T. AB Cable | 75 | 140 | 8.0 Mtr PSCC(140Kgs) | 16 | 65 | 3x16+25 Sqmm | 157900 | 41
28 | L.T. AB Cable | 100 | 140 | 8.0 Mtr PSCC(140Kgs) | 21 | 50 | 2x16+25 Sqmm | 157400 | 42
29 | L.T. AB Cable | 100 | 200 | 8.0 Mtr PSCC(200Kgs) | 16 | 65 | 3x16+25 Sqmm | 160200 | 43
30 | L.T. AB Cable | 100 | 200 | 8.0 Mtr PSCC(200Kgs) | 21 | 50 | 2x16+25 Sqmm | 160400 | 44
31 | Erection of 100KVA C.S.P Distribution transformer | [6 empty] | 249546 | 45
32 | Erection of 100KVA C.S.P Amorphous metal core Distribution transformer | [6 empty] | 249546 | 46
33 | Erection of 63 KVA C.S.P Distribution transformer | [6 empty] | 215701 | 47
34 | Erection of 63 KVA C.S.P Amorphous metal core Distribution transformer | [6 empty] | 215701 | 48
35 | Erection of 25KVA-11KV/433V copper wound DTR for releasing of Agricultural services (140Kgs PSCC Pole) | [6 empty] | 101869 | 49
36 | Erection of 25KVA-11KV/433V copper wound DTR for releasing of Agricultural services (200Kgs PSCC Pole) | [6 empty] | 102009 | 50
37 | Erection of 16KVA-11KV/433V copper wound DTR for releasing of Agricultural services (140Kgs PSCC Pole) | [6 empty] | 111754 | 51
38 | Erection of 16KVA-11KV/433V copper wound DTR for releasing of Agricultural services (200Kgs PSCC Pole) | [6 empty] | 111894 | 52
39 | Erection of 15 KVA Single Phase 6.3 KV/0-240V CSP OIL IMMERSED transformer | [6 empty] | 51573 | 53
40 | Erection of 15 KVA Single Phase 6.3 KV/0-240V Amorphous metal core transformer | [6 empty] | 51573 | 54
41 | Release of Single phase Water works Service erected on support | [6 empty] | 4104 | 55
42 | Release of poly phase Agl. Service erected on support | [6 empty] | 6923 | 56
43 | Release of single phase domestic and non domestic service with High Quality meter | [6 empty] | 4501 | 57
44 | Release of 3ph Domestic & Non-domestic service with High Quality meter | [6 empty] | 8100 | 58
45 | Release of poly phase Indl.service upto 15 H.P with High Quality meter | [6 empty] | 8936 | 59
46 | Release of poly phase Industrial service above 15 H.P to 50HP with C.T. operated meter | [6 empty] | 10458 | 60
47 | Erection of L.T. Electronic Trivector Meter on LV Side of DTR | [6 empty] | 13020 | 61
48 | Erection of Metering of LT industrial services load above 50HP to 75HP on 11KV side | [6 empty] | 160951 | 62
49 | Erection of Terminal & Metering Arrangement for 33KV Services with 33KV VCB | [6 empty] | 1270558 | 63
50 | Erection of 33/11 K.V. Substation with 1x5MVA power transformer & 3 Nos. 11kv feeders
| (with 11 kv 2 MVAR Capacitor Bank) | [6 empty] | 13091000 | 64-65
51 | Erection of 33/11 K.V. Substation with 1x5MVA power transformer & 2 Nos. 11kv feeders
| (without 11 kv 2 MVAR Capacitor Bank) | [6 empty] | 11455000 | 66-67
52 | Erection of 33/11 K.V. Substation with 1x5MVA power transformer & 3 Nos. 11kv feeders
| (without 11 kv 2 MVAR Capacitor Bank) | [6 empty] | 11807000 | 68-69
53 | Erection of 33/11 K.V. Substation with 1x5MVA power transformer & 4 Nos. 11kv feeders
| (without 11 kv 2 MVAR Capacitor Bank) | [6 empty] | 12160000 | 70-71
54 | Erection of 11KV Bay extension along with VCB in existing 33/11KV Sub-Station with RS Joists | [6 empty] | 557291 | 72
55 | Erection of 33KV Bay extension in existing 33/11KV Sub-Station | [6 empty] | 191782 | 73
56 | Erection of 5.0MVA Addl. PTR with 33KV Bay extension | [6 empty] | 4007674 | 74

## Materials
COST DATA OF CENTRALISED MAERIALS FOR R.E. AND DISTRIBUTION WORKS
2015-16
SL NO | SAP Material code | Description of materials | UNIT | Rupees | Latest rate | Latest LPO No/Date | Rupees | Consider rate
1) SUPPORTS AND FIXTURES, IRON, STEEL AND CEMENT
1.A) RS JOISTS
| MST00032 | RS JOIST 175X85MM | MT | 55347.05 |  |  | 55347.05
| MST00029 | RS JOIST 150X150MM | MT | 55347.05 | 40848 | 5100002884/10.8.15 | 55347.05
| MST00030 | RS JOIST 150X75MM | MT | 55347.05 |  |  | 55347.05
| MST00037 | RS JOIST 175 X 50 MM | MT | 55347.05 |  |  | 55347.05
1.B) PSCC POLES
| PLS00014 | PSCC SPUN POLES 12.5 MTS | EA | 11700 | 12200 | 51-2961/03.09.15 | 12200
| PLS00007 | PSCC SPUN POLES 11 MTS | EA | 10700 | 11300 | 51-2962/30.09.15 | 11300
| PLS00015 | PSCC Poles 11.0MTS | EA | 7600 |  |  | 7600
| PLS00004 | PSCC POLES 9.1 MTS 280KGS | EA | 3600 | 3640 | 51-2987/15.10.15 | 3640
| PLS00002 | PSCC POLES 8 MTS 200KGS | EA | 1980 | 1995 | 51-2789/17.10.15 | 1995
| PLS00001 | PSCC POLES 8 MTS 140KGS | EA | 1875 |  |  | 1875
| PLS00010 | RCC FENCING POLES 3 MTS | EA | 278.1 |  |  | 278.1
| PLS00009 | RCC FENCING POLES 2 MTS | EA | 113.3 |  |  | 113.3
| PLS00011 | RCC BASE PLATES | EA | 72.1 |  |  | 72.1
1.C) STEEL MATERIALS
| MST00012 | MS CHANNEL 100X50 | MT | 53886.51 | 39440 | 5100002805/4.7.15 | 53886.51
| MST00013 | MS CHANNEL 75X40 | MT | 53886.51 | 39300 | 5100002806/4.7.15 | 53886.51
| MST00011 | MS CHANNEL 150X75 | MT | 53886.51 |  |  | 53886.51
| MST00003 | MS ANGLE 65X65X6 | MT | 53886.51 | 38800 | 5100002774/19.6.15 | 53886.51
| MST00002 | MS ANGLE 50X50X6 | MT | 53886.51 | 38800 | 5100002774/19.6.15 | 53886.51
| MST00009 | MS ANGLE 130X130X12 | MT | 53886.51 |  |  | 53886.51
| MST00015 | MS FLAT 75X8 | MT | 53886.51 |  |  | 53886.51
| MST00014 | MS FLAT 50X6 | MT | 53886.51 |  |  | 53886.51
| MST00019 | MS ROD 20MM | MT | 53886.51 |  |  | 53886.51
| MST00018 | MS ROD 16MM | MT | 53886.51 |  |  | 53886.51
1.D) STEEL WIRE
| WRS00011 | HT STEEL WIRE 4MM | MT | 62191 |  |  | 62191
| WRS00006 | GI STAYWIRE 7/3.15MM (10 SWG) | MT | 65649 | 56250 | 5100002751/8.6.15 | 65649
| WRS00007 | GI STAYWIRE 7/2.5MM (12 SWG) | MT | 64839 | 57900 | 5100002751/8.6.15 | 64839
| WRS00005 | G.I. WIRE 4MM ( NO.8) | MT | 62300 |  |  | 62300
1.E) BOLTS AND NUTS
| BNT00028 | MS BOLTS & NUTS 5/8" X 6" | MT | 80628.4 |  |  | 80628.4
| BNT00031 | MS BOLTS & NUTS 5/8" X 9" | MT | 80628.4 |  |  | 80628.4
| BNT00024 | MS BOLTS & NUTS 5/8" X 2.5" | MT | 80628.4 |  |  | 80628.4
| BNT00025 | MS BOLTS & NUTS 5/8" X 3" | MT | 80628.4 | 53576 | 5100002750/5.6.15 | 80628.4
| BNT00026 | MS BOLTS & NUTS 5/8" X 4" | MT | 80628.4 | 53576 | 5100002750/5.6.15 | 80628.4
| BNT00006 | GI BOLTS & NUTS 1/2" X 1 1/2" | MT | 80628.4 |  |  | 80628.4
| BNT00009 | GI BOLTS & NUTS 3/8" X 1 1/2" | MT | 80628.4 |  |  | 80628.4
| BNT00022 | MS BOLTS & NUTS 5/8" X 1.5" | MT | 80628.4 |  |  | 80628.4
| BNT00023 | MS BOLTS & NUTS 5/8" X 2" | MT | 80628.4 |  |  | 80628.4
| BNT00030 | MS BOLTS & NUTS 5/8" X 8" | MT | 80628.4 |  |  | 80628.4
| BNT00035 | MS BOLTS & NUTS 3/8" X 1 1/2" FULL TH | MT | 80628.4 |  |  | 80628.4
| BNT00038 | MS BOLTS & NUTS 1/2"X1 1/2" | MT | 80628.4 |  |  | 80628.4
| BNT00043 | MS FULL NUTS 16MM (1" Thick) | MT | 80628.4 |  |  | 80628.4
| BNT00044 | MS HALF NUTS 16MM (1/2" Thick) | MT | 80628.4 |  |  | 80628.4
| BNT00045 | M.S.HEXAGONAL POLISHED NUTS 3/4 | MT | 80628.4 |  |  | 80628.4
1.F) CEMENT
| CEM00004 | OP CEMENT 53 GRADE FOR POLES | MT | 5871 | civil
2) INSULATORS AND HARDWARE
2.A) 33 KV
| INS30002 | 33KV SOLID CORE INSULATORS | EA | 1307.07 |  |  | 1307.07
| INS30004 | 33KV 70KN COMPOSITE POLYMER INSULATOR | EA | 648.9 | 323 | 5100002995/28.10.15 | 648.9
| INS30003 | 33KV POST TYPE INSULATORS (STAGS) | EA | 803.4 |  |  | 803.4
| INS30006 | 33KV 70KN DISC INSULATORS | EA | 391.4 |  |  | 391.4
| INS30001 | 33KV PIN INSULATORS | EA | 387 | 249.61 | 5100002970/21.9.15 | 387
| HWR00003 | 33KV GI PINS | EA | 162.74 | 139.8 | 5100002934/31.8.15 | 162.74
| HWR00004 | 33KV METAL PARTS (B&S) | SET | 180 | 173.59 | 5100002972/21.9.15 | 180
2.B) 11 KV
| INS10006 | 11KV SOLID CORE INSULATORS FOR AB SWITCH | EA | 221 | 252 | 5100002938/31.8.15 | 252
| INS10007 | 11KV SOLID CORE INSULATORS FOR HG FUSES | EA | 133.9 | 163.2 | 5100002747/1.6.15 | 163.2
| INS10009 | 11KV POLYMER INSULATORS (B&S) | EA | 257.5 |  |  | 257.5
| INS10003 | 11KV POLYMER INSULATORS (C&T) | EA | 195.7 | 135.72 | 5100002735/29.5.15 | 195.7
| INS10011 | 11 KV POLYMER DISC | EA | 257.5 |  |  | 257.5
| INS10008 | 11KV POST TYPE INSULATORS | EA | 232.78 |  |  | 232.78
| INS10004 | 11KV DISC INSULATORS (B&S) | EA | 206 |  |  | 206
| INS10002 | 11KV DISC INSULATORS (C&T) | EA | 216.3 |  |  | 216.3
| INS10001 | 11KV PIN INSULATORS | EA | 54 | 44.46 | 5100003002/27.5.15 | 54
| HWR00001 | 11KV GI PINS | EA | 59 | 54.4 | 5100002723/27.5.15 | 59
| HWR00002 | 11KV METAL PARTS (C&T) | SET | 82.4 | 76.51 | 5100003067/27.1.16 | 82.4
| INS10005 | 11KV GUY INSULATORS (HT) | EA | 41 | 36 | 5100002936/31.8.15 | 41
2.C) LT
| INS00001 | LT PIN INSULATORS | EA | 11 | 13.95 | 5100002936/31.8.15 | 13.95
| HWR00015 | LT GI PINS | EA | 28.84 | 25.71 | 5100002869/7.8.15 | 28.84
| INS00002 | LT SHACKLES | EA | 12 | 12.24 | 5100002832/15.7.15 | 12.24
| HWR00016 | LT METAL PARTS | SET | 31.93 | 31.4 | 5100002721/27.5.15 | 31.93
| INS00005 | BUS-BAR INSULATORS WITH ALUMINIUM STRIP | EA | 61.8 |  |  | 61.8
| INS00003 | LT GUY INSULATORS | EA | 12 | 18 | 5100002937/31.8.15 | 18
3) CROSS ARMS
3.A) 33 KV CROSS ARMS AND TOP FITTINGS
| FBE00026 | 33KV TAPING CHANNEL X ARMS | EA | 1112.4 |  |  | 1112.4
| FBE30003 | 33KV V CROSS ARMS WITH CLAMPs | EA | 1175 | 1197 | 5100002886/10.8.15 | 1197
| FBE30004 | 33KV V CROSS ARMS WITHOUT CLAMPS | EA | 1025.88 |  |  | 1025.88
| FBE30018 | 33KV CHANNEL V X ARMs FOR SPUN POLE WITH CLAMPs | EA | 1352.39 |  |  | 1352.39
| FBE30006 | 33KV TOP CLEAT WITH CLAMPs | EA | 519.12 |  |  | 519.12
3.B) 11KV CROSS ARMS AND TOP FITTINGS
| FBE10004 | 11KV M.S CHANNEL CROSS ARM(TAPPING)75X40 | EA | 545 |  |  | 545
| FBE10006 | 11KV HORIZONTAL CROSS ARMS | EA | 463.5 |  |  | 463.5
| FBE10033 | 11KV TAPPING X ARM W 100X50MM MS CHANNEL | EA | 648.9 |  |  | 648.9
| FBE10035 | 11KV MS CH X ARM(TAPING)75X40 WITH CLAMP | EA | 492.34 |  |  | 492.34
| FBE10001 | 11KV ANGLE V-X ARMS 65X65X6 W/O CLAMPS | EA | 477.92 |  |  | 477.92
| FBE10002 | 11KV VX ARMS WITH MSCHANNEL 140KG | EA | 574.74 |  |  | 574.74
| FBE10003 | 11KV VCROSS ARMS WITH CLAMPS 200KG | EA | 574.74 | 443 | 5100002857/4.8.15 | 574.74
| FBE10016 | 11KV V 'X' ARM(75X40) WITH CLAMP FOR 9.1 | EA | 549 | 478 | 5100002959/1.9.15 | 549
| FBE10028 | 11KV ANGLE V-X ARM WITH CLAMP 140 KG | EA | 533 |  |  | 533
| FBE10034 | 11KV ANGLE V-X ARM WITH CLAMP 200 KG | EA | 533 | 443 | 5100002843/4.8.15 | 533
| FBE00025 | 11 KV SIDE ARM WITH STUTT | EA | 1205.1 |  |  | 1205.1
| FBE10007 | 11KV TOP CLEAT WITH CLAMPS For 8.0 | EA | 281.19 | 195.25 | 5100002843/21.7.15 | 281.19
| FBE10021 | 11KV TOP CLEAT WITH CLAMPS FOR 9.1 | EA | 281 | 220 | 5100002883/10.8.15 | 281
| FBE10032 | 11KV Spl. Type Top Fittings with Clamps | EA | 175.1 |  |  | 175.1
3.C) LT CROSS ARMS
| FBE00008 | LT 3 PH. 5 WIRE CROSS ARMS | EA | 381.1 |  |  | 381.1
| FBE00039 | LT RAISING 3-PHASE 5 WIRE CROSS ARM | EA | 1215.4 |  |  | 1215.4
| FBE00020 | LT 3PH 4 WIRE X ARMS WITHOUT CLAMP | EA | 247.2 |  |  | 247.2
| FBE00007 | LT 3 PH 4WIRE CROSS ARM & CLAMP (200KG) | EA | 371.83 | 303 | 510002875/10.8.15 | 371.83
| FBE00009 | LT 3 PH 4WIRE CROSS ARM & CLAMP (140KG) | EA | 371.83 |  |  | 371.83
| FBE00030 | LT 3PH ANGLE X-ARM W CLAMP[50X50X6] 140KG | EA | 226.6 |  |  | 226.6
| FBE00036 | LT 3PH SIDE ARMS WITH STUTT | SET | 824 |  |  | 824
| FBE00045 | LT 3PH SIDE ARMS WITH STUTT & CLAMPS | SET | 885.8 |  |  | 885.8
| FBE00034 | LT 1 PH. 3 WIRE CROSS ARM WITHOUT CLAMP | EA | 319.3 |  |  | 319.3
| FBE00006 | LT 1 PH. 3 WIRE CROSS ARM WITH CLAMP | EA | 391.4 | 233 | 510002837/21.7.15 | 391.4
| FBE00029 | LT 1PH 3 W ANGLE X-ARM W CLAMP [50X50X6) | EA | 391.4 |  |  | 391.4
| FBE00033 | LT 1 PH. 2 WIRE CROSS ARMS W/O CLAMP | EA | 267.8 |  |  | 267.8
| FBE00024 | LT STUT AND SIDE ARM | EA | 1009.4 |  |  | 1009.4
3.D) BACK CLAMPS
| FBE30001 | 33KV M.S.BACK CLAMPS | EA | 139.05 |  |  | 139.05
| FBE30024 | 33KV M.S.BACK CLAMPS FOR SPUN POLES | EA | 161.71 |  |  | 161.71
| FBE30002 | 33KV M.S.STAY CLAMPS | EA | 218.36 |  |  | 218.36
| FBE00002 | M.S.BACK CLAMPS FOR 9.1 M PSCC POLE | EA | 99.91 |  |  | 99.91
| FBE00040 | M.S.BACK CLAMPS FOR 9.1 M POLE 75X8 | EA | 97.85 |  |  | 97.85
| FBE00001 | M.S.BACK CLAMPS FOR 8 MPSCC POLES 200KG | EA | 72.1 |  |  | 72.1
| FBE00041 | MS.BACK CLAMP 8M POLES 200KG(SLOT HOLE) | EA | 72.1 |  |  | 72.1
| FBE00048 | MS STRUT CLAMPS FOR 8M/200KG POLES (SET) | EA | 77.25 |  |  | 77.25
| FBE00038 | MS STAY CLAMP FOR 140 KG POLE | EA | 72.1 |  |  | 72.1
| FBG00019 | M.S.STAY CLAMPS SPECIAL | EA | 72.1 |  |  | 72.1
| FBE00021 | POLE MOUNTING CLAMPS | EA | 36.05 |  |  | 36.05
3.E) STAY SETS
| FBE30008 | 33KV MS STAY SETS WITH BASE PLATE | EA | 432.6 |  |  | 432.6
| FBE30009 | 33KV MS STAY SETS WITHOUT BASEPLATE | EA | 360.5 | 366 | 5100002895/10.8.15 | 366
| FBE30010 | 33KV MS STAY SET WITHOUT CLAMPS | EA | 525.3 |  |  | 525.3
| FBE30021 | 33KV MS STAY SET WITH CLAMPS For 9.1MTS POLES |  | 778.68 |  |  | 778.68
| FBE10022 | 11KV MS STAY SET WITH CLAMPS | EA | 448.05 |  |  | 448.05
| FBE10010 | 11KV MS STAY SETS WITHOUT BASEPLATE | EA | 385 |  |  | 385
| FBE10023 | 11KV MS STAY SETS WITH OUT CLAMPS | SET | 226.6 |  |  | 226.6
| FBE00004 | M.S.STAY CLAMPS FOR 9.1 M PSCC POLE | EA | 144.2 |  |  | 144.2
| FBE00028 | M.S.STAYSET WITH CLAMPS FOR 8M PSCCPOLES | EA | 319.3 |  |  | 319.3
| FBE00003 | M.S.STAY CLAMPS FOR 8 MPSCC POLES (SET) | EA | 82.4 |  |  | 82.4
3.F) DP STRUCTURE MATERIALS
| FBG00032 | DP STRUCTURE TOTAL SET | SET | 3924.3 |  |  | 3924.3
| FBG00010, FBG00018 | POLE MOUNT ARGMT FOR 16/25KVADTR(CHANEL) | EA | 2018.8 |  |  | 2018.8
| FBE00044 | MOUNTING ARRANGEMENT FOR 1PH DTR | SET | 356 |  |  | 356
4) CONDUCTORS
| CDR00005 | AAA CONDUCTOR 200 SQ. MM | KM | 132334.4 |  |  | 132334.4
| CDR00004 | AAA CONDUCTOR 100 SQ. MM | KM | 50953 | 45575 | 5100003046/29.12.15 | 50953
| CDR00003 | AAA CONDUCTOR 55 SQ. MM | KM | 29490 | 24900 | 5100002851/28.7.15 | 29490
| CDR00002 | AAA CONDUCTOR 34 SQ. MM | KM | 17685 | 17480.46 | 5100002827/14.7.15 | 17685
| CDR00011 | ACSR CONDUCTOR ZEBRA | KM | 234819.4 |  |  | 234819.4
| CDR00010 | ACSR CONDUCTOR PANTHER 200 Sq.mm | KM | 131077.8 |  |  | 131077.8
| CDR00008 | ACSR CONDUCTOR (30+7/3.00MM) 200 SQMM | KM | 130974.8 |  |  | 130974.8
| CDR00006 | ACSR CONDUCTOR 7/2.11 | KM | 12730.8 |  |  | 12730.8
| CDR00014 | AL 59 CONDUCTOR 109 SQ MM | KM | 47009.2 |  |  | 47009.2
5) CABLES
5.A) 33 KV XLPE POWER CABLES
| CBX30001 | 33KV XLPE CABLE 3 CORE 400 SQ. MM | M | 1957 |  |  | 1957
| CBX30004 | 33KV XLPE CABLE 3 CORE 300 SQ. MM | M | 1699.5 |  |  | 1699.5
5.B) 11 KV XLPE POWER CABLES
| CBX10008 | 11KV XLPE CABLE 3 CORE 300 SQ. MM | M | 1236 |  |  | 1236
| CBX10007 | 11KV XLPE CABLE 3 CORE 185 SQ. MM | M | 927 |  |  | 927
| CBX10006 | 11KV XLPE CABLE 3 CORE 120 SQ. MM | M | 710.7 |  |  | 710.7
| CBX10005 | 11KV XLPE CABLE 3 CORE 95 SQ. MM | M | 566.5 |  |  | 566.5
| CBX10002 | 11KV XLPE CABLE 3 CORE 35 SQ. MM | M | 339.9 | 316.427 | 5100002957/31.8.15 | 339.9
5.C) 11 KV PLIC POWER CABLES
| CBX10001 | 11KV PLIC CABLE 3 CORE 35 SQ. MM | M | 298.7 |  |  | 298.7
5.D) LT PVC 1 CORE CABLES (XLPE)
279 | CBX00017 | LT PVC CABLE 1 CORE 185 SQ. MM | M | 118.45 |  |  | 118.45
| CBX00009 | LT PVC CABLE 1 CORE 150 SQ. MM | M | 94.76 | 94.803 | 5100002275/16.6.14 | 94.76
| CBX00008 | LT PVC CABLE 1 CORE 120 SQ. MM | M | 79 | 78.42 | 5100002275/16.6.14 | 79
| CBX00007 | LT PVC CABLE 1 CORE 95 SQ. MM | M | 62.83 | 63.438 | 5100002996/28.10.15 | 64
| CBX00006 | LT PVC CABLE 1 CORE 70 SQ. MM | M | 46.35 |  |  | 46.35
| CBX00005 | LT PVC CABLE 1 CORE 50 SQ. MM | M | 36.05 |  |  | 36.05
5.E) LT XLPE 1 CORE CABLES
| CBX00002 | LT XLPE CABLE 1 CORE 70 SQ. MM | M | 46.35 |  |  | 46.35
5.F) LT XLPE 3 1/2 CORE CABLES
| CBX00015 | LT XLPE CABLE 3 1/2 CORE 185 SQ. MM | M | 329.6 |  |  | 329.6
| CBX00014 | LT XLPE CABLE 3 1/2 CORE 120 SQ. MM | M | 302.82 |  |  | 302.82
| CBX00013 | LT XLPE CABLE 3 1/2 CORE 95 SQ. MM | M | 236.9 |  |  | 236.9
| CBX00012 | LT XLPE CABLE 3 1/2 CORE 70 SQ. MM | M | 190.55 |  |  | 190.55
| CBX00018 | LT PVC AL CONTR CABLE 4 CORE 4 SQ. MM | M | 25.75 |  |  | 25.75
5.G) LT UNARMOURED 3 1/2 CORE CABLES
| CBP00019 | LT PVC UNARMOURED 3.5 CORE CABLE 150sqmm | M | 339.9 |  |  | 339.9
5.H) LT CONTROL CABLES
| CBP00006 | LT PVC CU CONTR CABLE 10 CORE 2.5 SQ. MM | M | 160.68 | 164.6 | 5100002811/7.7.15 | 164.6
| CBP00002 | LT PVC CU CONTR CABLE 4 CORE 2.5 SQ. MM | M | 65.92 | 68.22 | 5100002811/7.7.15 | 68.22
| CBP00001 | LT PVC CU CONTR CABLE 2 CORE 2.5 SQ. MM | M | 37 | 38.22 | 5100002811/7.7.15 | 38.22
| CBX00018 | LT PVC AL CONTR CABLE 4 CORE 4 SQ. MM | M | 26 |  |  | 26
5.I) LT AERIAL BUNCHED CABLES
| CBA00003 | LT AB CABLE 3 X 16 + 25 SQ. MM | M | 49 | 46.77 | 510002769/18.6.15 | 49
| CBA00002 | LT AB CABLE 2 X 16 + 25 SQ. MM | M | 33 | 34.35 | 5100002729/27.5.15 | 34.35
| CBA00001 | LT AB CABLE 1 X 16 + 25 SQ. MM | M | 25.75 |  |  | 25.75
5.J) LT AERIAL BUNCHED CABLE FITTINGS
| HWR00012 | HARDWARE FOR SUSPENSION CLAMPS(EYEHOOKS) | EA | 175.1 |  |  | 175.1
| SCB00058 | LT CONNECTOR FOR AB CABLE WTH Insulation | EA | 82.4 |  |  | 82.4
| HWR00009 | DEAD END CLAMPS WITH EYE HOOK | EA | 113.3 |  |  | 113.3
5.K) CABLE JOINTING KITS
| SCB00069 | 33KV 3X400 XLPE UG CABLE ST TH JOINT KIT | EA | 45088.25 |  |  | 45088.25
| SCB00061 | 33KV XLPE CABLE JOINTING KIT 3X400SQMM | EA | 10351.5 |  |  | 10351.5
| SCB00027 | 11KV HEAT SHRKABL JOIT.KIT FOR 3X300SQMM | EA | 0 |  |  | 0
| SCB00055 | 11KV CABLE JOINTING KITS 3X185 SQ.MM | EA | 2925.2 |  |  | 2925.2
| SCB00025 | 11KV CABLE JOINTING KIT 3X35SQMM OUTDOOR | EA | 772.5 | 584 | 5100002958/31.8.15 | 772.5
6) POWER TRANSFORMERS, CAPACITORS AND TRASFORMER OIL
| PTR00009 | 33/11 KV 10MVA POWER TRANSFORMER | EA | 5386320 |  |  | 5386320
| PTR00008 | 33/11 KV 8MVA POWER TRANSFORMER | EA | 4535000 | 4225206 | 5100003065/12.1.16 | 4535000
| PTR00006 | 33/11 KV 5MVA POWER TRANSFORMER | EA | 3345440 | 3297378.84 | 5100002641/24.2.15 | 3345440
| PTR00005 | 33/11 KV 3.15MVA POWER TRANSFORMER | EA | 2856190 |  |  | 2856190
| CPT10013 | 11KV CAPACITOR BANK WITH VCB & ACCESSORIES | EA | 1013247.05 | 8400001.5 | 5100003077/5.2.16 | 1013247.05
| OFO10009 | TRANSFORMER OIL (with Drums) | L | 79.31 | 56.8 | 5100002680/26.3.15 | 79.31
7) DISTRIBUTION TRANSFORMERS
7.A) 3PH DTRs
| DTC30009 | 3PH 315KVA DTR CRGO CSP | EA | 553440 | 516705 | 5100002772/19.6.15 | 553440
| DTA30013 | 3PH 315KVA DTR AMARPHOUS CSP | EA | 553440 |  |  | 553440
| DTC30011 | 3PH 250KVA DTR CRGO CSP | EA | 315618 |  |  | 315618
| DTC30113 | 3PH 250KVA DTR CRGO CONVENTIONAL | EA | 315618 |  |  | 315618
| DTA30007 | 3PH 160KVA DTR AMARPHOUS | EA | 233940 |  |  | 233940
| DTC30127 | 3PH 160KVA DTR AMARPHOUS/CRGO CSP BEE 5* RATING | EA | 233940 | 217200 | 5100002757/9.6.15 | 233940
| DTC30007 | 3PH 160KVA DTR CRGO CSP | EA | 233940 |  |  | 233940
| DTC30118 | 3-PH 160 KVA DTR WITH BEE BEE 3* RATING | EA | 233940 |  |  | 233940
| DTC30106 | 3PH 100KVA DTR CRGO CONVENTIONAL | EA | 142800 |  |  | 144149.79
| DTA30006 | 3PH 100KVA DTR AMARPHOUS | EA | 142800 |  |  | 144149.79
| DTC30131 | 3PH 100KVA DTR AMARPHOUS/CRGO with 5 star | EA | 142800 | 137878.22 | 5100002779/20.6.15 | 144149.79
| DTC30006 | 3PH 100KVA DTR CRGO CSP | EA | 142800 |  |  | 144149.79
| DTC30116 | 3PH 100KVA DTR CRGO CONV BEE 3* RATING |  | 142800 |  |  | 144149.79
| DTC30122 | 3PH 100KVA DTR CRGO CONV BEE 5* RATING | EA | 142800 | 144149.79 | 5100003058/12.1.16 | 144149.79
| DTC30005 | 3PH 75 KVA DTR CRGO CSP | EA | 91928 |  |  | 91928
| DTC30105 | 3PH 75 KVA DTR CRGO CONVENTIONAL | EA | 91928 |  |  | 91928
| DTC30104 | 3PH 63 KVA DTR CRGO CONVENTIONAL | EA | 115200 |  |  | 115200
| DTC30004 | 3PH 63 KVA DTR CRGO CSP | EA | 115200 |  |  | 115200
| DTA30004 | 3PH 63 KVA DTR AMARPHOUS | EA | 115200 |  |  | 115200
| DTC30129 | 3PH 63 KVA DTR AMARPHOUS CSP BEE 5* RATING | EA | 115200 | 107400 | 5100002768/18.6.15 | 115200
| DTC30115 | 3PH 63 KVA DTR CRGO CONV BEE 3* RATING | EA | 115200 |  |  | 115200
| DTC30003 | 3PH 50 KVA DTR CRGO CSP | EA | 69010 |  |  | 69010
| DTC30103 | 3PH 50 KVA DTR CRGO CONVENTIONAL | EA | 69010 |  |  | 69010
| DTC30111 | 3PH 40 KVA DTR CRGO CONV BEE 3* RATING | EA | 98350 |  |  | 98350
| DTC30128 | 3PH 40 KVA DTR CRGO CONVL BEE 3* RATING | EA | 98350 |  |  | 98350
| DTC30130 | 3PH 40 KVA DTR AMARPHOUS CONV BEE 5* RATING | EA | 98350 | 95998.01 | 5100002894/5.8.15 | 98350
| DTC30102 | 3PH 25 KVA DTR CRGO CONVENTIONAL | EA | 61216 |  |  | 61216
| DTC30116 | 3PH 25 KVA DTR CRGO CONV BEE 3* RATING | EA | 61216 | 51520 | 5100002730/30.5.15 | 61216
| DTC30123 | 3PH 25 KVA DTR CRGO CONV BEE 5* RATING | EA | 61216 |  |  | 61216
| DTC30002 | 3PH 25 KVA DTR CRGO CSP | EA | 61216 |  |  | 61216
| DTC30101 | 3PH 16 KVA DTR CRGO CONV 3* RATING | EA | 53857 |  |  | 53857
| DTC30001 | 3PH 16 KVA DTR CRGO CSP | EA | 53857 |  |  | 53857
| DTC30132 | 3PH 16 KVA DTR CRGO/AMARPHOUS CONV 5* RATING (COPPER) | EA | 69668 |  |  | 69668
| DTC30112 | 3PH 15 KVA DTR CRGO CONVENTIONAL | EA | 37080 |  |  | 37080
| DTA30011 | 3PH 15 KVA DTR AMARPHOUS | EA | 37080 |  |  | 37080
| DTC10001 | 1PH 5 KVA DTR CRGO CSP | EA | 24139 | 23735.52 | 5100002801/30.6.15 | 24139
| DTC10101 | 1PH 5 KVA DTR CRGO CONVENTIONAL | EA | 24139 |  |  | 24139
| DTC10002 | 1PH 10 KVA DTR CRGO CSP | EA | 27501 |  |  | 27501
| DTC10103 | 1PH 10 KVA DTR 11KV/1.732 CRGO CONV | EA | 27501 |  |  | 27501
| DTC10004 | 1PH 15 KVA DTR CRGO CSP | EA | 37522 |  |  | 37522
| DTA10003 | 1PH 15 KVA DTR AMARPHOUS | EA | 37522 |  |  | 37522
| DTC10104 | 1PH 15 KVA DTR CRGO CONVENTIONAL | EA | 37522 |  |  | 37522
| DTC10107 | 1PH 16 KVA DTR CRGO/AMARPHOUS CSP | EA | 45810 | 48849.99 | 5100003061/12.1.16 | 48849.99
8) SWITCH CONTROL AND PROTECTIVE GEAR
8.A) CIRCUIT BREAKERS AND RELAYS
| BRK30001 | 33KV SF6 CIRCUIT BREAKER W/O PANEL | EA | 360706 |  |  | 360706
| BRK30002 | 33KV FEEDER VCB WITH CT'S&CONTROL PANEL | EA | 345256 |  |  | 345256
| BRK30016 | 33KV Feder VCB W/O CT's&with Contl Panel | EA | 283677.45 | 275415 | 5100001984/1.11.13 | 283677.45
| BRK30017 | 33KV SF6 CIRCUIT BREAKER CONTROL PANEL | EA | 212180 |  |  | 212180
| BRK30005 | 33KV VCB W/O CT'S&CONTROL PANEL(220V DC) | EA | 206866.23 |  |  | 206866.23
| BRK30003 | 33KV VCB W/O CT'S&CONTROL PANEL(24V DC) | EA | 275415 | 275415 | 5100001615/29.4.13 | 275415
| BRK30019 | 33KV FEEDER VCB Without CONTROL RELAY PANEL | EA | 312750 | 312750 | 5100002492/27.11.14 | 312750
| BRK30020 | 33KV VCB WITH CT'S&CONTROL PANEL (24V) | EA |  | 454563.22 | 5100002663/09.03.15 | 454563
| BRK10002 | 11KV FEEDER VCB WITH CT'S&CONTROL PANEL | EA | 245528 | 237000 | 5100002662/9.3.15 | 245528
| BRK10010 | 11KV LV CONTROL VCB WITH RELAY PANEL | EA | 172283.98 | 254666.78 | 5100002066/23.1.14 | 254666.78
| BRK10004 | 11KV LV VCB with CTs and Control panels | EA | 278542.9 | 271080.42 | 5100002661/9.3.15 | 278543
| BRK10011 | 11KV FEEDER CONTROL VCB WITH RELAY PANEL | EA | 166729.19 | 154385 | 5100001986/1.11.13 | 166729.19
8.B) SWITCH GEAR ACCOSSIORIES
| BRK30014 | 33KV TWIN FEDR CONTL&RELY PANEL(220V DC) | EA | 147135.5 | 144217.52 | 5100002494/27.11.14 | 147135.5
| BRK30013 | 33KV HV/LV RELAY PANEL | EA | 84696.9 |  |  | 84696.9
| BRK30011 | 33KV CONTROL PANEL WITH ENERGY METER | EA | 78496.3 |  |  | 78496.3
| BRK30010 | 33KV CONTROL PANEL WITHOUT ENERGY METER | EA | 74263 |  |  | 74263
| BRK30012 | 33KV INDOOR CONTROL PANEL | EA | 46216.1 |  |  | 46216.1
| BRK00002 | 11KV RING MAIN UNITS 5 WAY | EA | 642720 |  |  | 642720
| BRK10006 | 11KV 220V RELAY CONTROL PANEL | EA | 124321 |  |  | 124321
| BRK10012 | 11KV FEEDER CONTROL RELAY PANEL | EA | 39964 |  |  | 39964
| BRK10008 | ALARAM PANEL SUITABLE FOR 11KV | EA | 29174.75 |  |  | 29174.75
9) CURRENT TRANSFORMERS
9.A) 33 KV CTs
| ITR30031 | 33KV CT'S 200-100-50/1-1A | EA | 18570.9 |  |  | 18570.9
| ITR30032 | 33KV CT'S 200-100-50/5-5A | EA | 18158.9 |  |  | 18158.9
| ITR30034 | 33KV CT'S 400-200-100/1-1-1A | EA | 18534.85 | 20448.91 | 5100002816/8.7.15 | 20448.91
| ITR30035 | 33KV CT'S 400-200-100/1-1A | EA | 20702 | 22545.54 | 5100002816/8.7.15 | 22545.54
| ITR30036 | 33KV CT'S 400-200-100/5-5A | EA | 18158.9 |  |  | 18158.9
| ITR30037 | 33KV CT'S 200-100/ 1-1 A | EA | 18158.9 |  |  | 18158.9
| ITR30070 | 33KV METERING CT'S 100/1A Class 1.0 | EA | 18035.3 |  |  | 18035.3
| ITR30071 | 33KV METERING CT'S 25/1A 0.2 CL | EA | 16084 | 16894.95 | 5100002582/9.1.15 | 16894.95
| ITR30072 | 33KV METERING CT'S 50/1A 0.2 CL | EA | 20126.2 | 16894.95 | 5100002582/9.1.15 | 20126.2
| ITR30073 | 33KV METERING CT'S 100/1A 0.5 CLASS | EA | 18035.3 |  |  | 18035.3
| ITR30074 | 33KV METERING CT'S 100/1A 0.2 CLASS | EA | 18859.3 |  |  | 18859.3
| ITR30075 | 33KV 1PH OUTDOOR CT RATIO 100-50/5-5A | EA | 18035.3 |  |  | 18035.3
| ITR30076 | 33KV CTs 200-100/1-1-1Amps | EA | 16377 |  |  | 16377
| ITR30077 | 33KV CTs - 150/1.1Amps | EA | 15171.9 |  |  | 15171.9
| ITR30078 | 33KV CTs 200/1A CLASS 0.2 | EA | 23391.3 | 15732.62 | 5100002812/8.7.15 | 23391.3
| ITR30079 | 33 KV INDOOR EPOXY RESIN CAST CT | EA | 23896 |  |  | 23896
| ITR30080 | 33KV CTs 200/1A CLASS 0.2S ACCURACY | EA | 20280.7 |  |  | 20280.7
| ITR30101 | 33KV METRNG CT 50/1A CLASS 0.2S ACCURACY | EA | 16895 | 15732.62 | 5100002812/8.7.15 | 16895
| ITR30110 | 33KV METRNG CT 100/1A CLASS 0.2S ACCURACY | EA | 15903 |  |  | 15903
| ITR30104 | 33KV METRNG CT 150/1A CLASS 0.2S ACCURACY | EA | 15903 | 15732.62 | 5100002812/8.7.15 | 15903
| ITR30111 | 33KV METRNG CT 25/1A CLASS 0.2S ACCURACY | EA | 16895 | 15732.62 | 5100002812/8.7.15 | 16895
9.B) 33 KV PTs
| ITR30011 | 33KV 1PH P.T.S 100VA BURDEN CLASS 0.5 | EA | 17253 |  |  | 17253
| ITR30012 | 33KV 1PH P.T.S 100VA BURDEN CLASS 0.2 | EA | 21628 |  |  | 21628
| ITR30100 | 33KV 1PH 200VA PT class 1.00 | EA | 11845 |  |  | 11845
| ITR30015 | 33KV 1PH P.T.S 110V, 10VA BURDEN | EA | 20909 | 18900 | 5100002758/15.6.15 | 20909
9.C) 11 KV CTs
| ITR10005 | 11 KV CT 200-100/1-1A (METERING CORE) | EA | 8827.1 |  |  | 8827.1
| ITR10006 | 11 KV CT 200-100/5-5A (METERING CORE) | EA | 11463.9 |  |  | 11463.9
| ITR00009 | 11 KV CTS -600-300/1.A | EA | 15657.03 |  |  | 15657.03
| ITR10010 | 11 KV CT 50-100/1A | EA | 8198.8 |  |  | 8198.8
| ITR10011 | 11 KV CT 600-300-150/1A | EA | 9630.5 |  |  | 9630.5
| ITR10012 | 11KV CT'S 50-100/5A | EA | 8198.8 |  |  | 8198.8
| ITR10050 | 11KV CT'S 100-50/5A | EA | 7333.6 |  |  | 7333.6
| ITR10051 | 11KV CT'S 200-100/5-5A | EA | 8538.7 |  |  | 8538.7
| ITR10052 | 11KV CT'S 200-100-50/5-5A | EA | 11566.9 |  |  | 11566.9
| ITR10053 | 11KV CT'S 400-200/1-1A | EA | 11051.9 | 14155 | 5100002814/8.7.15 | 14155
| ITR10055 | 11KV CT'S 400-200-100/1-1A | EA | 14389.1 | 14899.55 | 5100002813/8.7.15 | 14899.55
| ITR10056 | 11KV CT'S 400-200-100/5-5A | EA | 13791.7 |  |  | 13791.7
| ITR10057 | 11KV CT'S 600-300-150/1-1-0.5775A | EA | 15199.71 | 16774 | 5100002813/8.7.15 | 16774
| ITR10071 | 11KV POLYCRETE CT RATIO 200-100/1-1A | EA | 8178.2 |  |  | 8178.2
| ITR10072 | 11KV POLYCRETE CT RATIO 200-100/5-5A | EA | 8827.1 |  |  | 8827.1
| ITR10073 | 11KV CTs - 200 - 150 / 1.1A | EA
9.D) 11 KV PTs
| ITR10020 | 11KV 3PH P.T.S | EA | 18334 |  |  | 18334
9.E) 11 KV CTPT sets
| ITR10032 | 11KV C.T.P.T. SET 75/5A | EA | 39965 | 39500 | 5100002760/15.6.15 | 39965
| ITR10029 | 11KV C.T.P.T. SET 60/5A | EA | 44502 | 39500 | 5100002760/15.6.15 | 44502
| ITR10028 | 11KV C.T.P.T. SET 40/5A | EA | 39965 | 39500 | 5100002760/15.6.15 | 39965
| ITR10026 | 11KV C.T.P.T. SET 20/5A | EA | 39965 | 39500 | 5100002760/15.6.15 | 39965
| ITR10025 | 11KV C.T.P.T. SET 10/5A | EA | 39965 | 39600 | 5100002762/15.6.15 | 39965
| ITR10083 | 11KV C.T.P.T. SET 5/5A | EA | 32496.5 | 28123.76 | 5100001895/8.8.13 | 32496.5
| ITR10035 | 11KV BOTH SIDE CABLE ENTRY INDOOR 10/5A | EA | 32418.22 | 40900 | 5100002759/15.6.15 | 40900
| ITR10036 | 11KV BOTH SIDE CABLE ENTRY INDOOR 20/5A | EA | 31930 | 40900 | 5100002759/15.6.15 | 40900
| ITR10037 | 11KV OD PL MOUNT CTPT 60/5A 80KA 0.5SEC | EA | 31044.2 |  |  | 31044.2
| ITR10075 | 11KV CTS OF RATIO 600-300/1-1-0.5775A | EA | 15429.4 |  |  | 15429.4
| ITR30102 | 11 KV, 20/5A NEUTRAL CURRENT TRANSFORMER | EA | 47740.5 |  |  | 47740.5
| ITR30103 | 11 KV/110V RESIDUAL VOLTAGE TRANSFORMER | EA | 47740.5 |  |  | 47740.5
| ITR40001 | 3PH 0-500V 30V VARRIAC | EA | 18334 |  |  | 18334
| ITR40002 | CONSTANT VOLTAGE TRS. 150V 3A BHEL | EA
10) AB SWITCHES
10.A) 33 KV
| ABS30010 | 33KV 800A CONV. AB SWITCH WITH S.C.I | EA | 39800 |  |  | 39800
| ABS30004 | 33KV 800A CONV. AB SWITCH WITH P.T.I | EA | 27279.55 |  |  | 27279.55
| ABS30007 | 33KV 800A ABSWITCH 100A FUSE TY WITH INS | EA | 22763 |  |  | 22763
| ABS30009 | 33KV 800A ABSWITCH 75A FUSE TY WITH INSL | EA | 22763 |  |  | 22763
| ABS30008 | 33KV 800A ABSWITCH 40A FUSE TY WITH INSL | EA | 22886.6 |  |  | 22886.6
| ABS30002 | 33KV 400A AB SWITCH WITH INSULATORS | EA | 21537.3 |  |  | 21537.3
10.B) 11KV
| ABS10015 | 11KV 800A CONV. AB SWITCH WITH P.T.I | EA | 15887.75 |  |  | 15887.75
| ABS10014 | 11KV 800A D/B AB SWITCH W/O INSULATORS | EA | 12658.7 |  |  | 12658.7
| ABS10008 | 11KV 400A CONV AB SWITCH WITH P.T.I | EA | 10623.42 | 7750 | 5100002861/7.8.15 | 10623.42
| ABS10007 | 11KV 400A CONV AB SWITCH W/O INSULATORS | EA | 4604.1 |  |  | 4604.1
| ABS10002 | 11KV 200A TT AB SWITCH WITH INSULATORS | EA | 8322.4 | 8250 | 5100002785/23.6.15 | 8322.4
| ABS10001 | 11KV 200A TT AB SWITCH W/O INSULATORS | EA | 5582.6 |  |  | 5582.6
| ABS10004 | 11KV 200A CONV AB SWITCH WITH P.T.I | EA | 9012.5 | 7320 | 5100002862/7.8.15 | 9012.5
| ABS10003 | 11KV 200A CONV AB SWITCH W/O INSULATORS | EA | 4120 |  |  | 4120
11) LIGHTNING ARRESTORS
| LAS00004 | 33KV LIGHTNING ARRESTORS STATION TYPE | EA | 4460 | 3474.98 | 5100003007/28.10.15 | 4460
| LAS00002 | 11KV LIGHTNING ARRESTORS STATION TYPE | EA | 2977 | 1985.2 | 5100002994/28.10.15 | 2977
| LAS00001 | 11KV LIGHTNING ARRESTORS LINE TYPE | EA | 1473 | 335.64 | 5100002997/28.10.15 | 1473
12) HG FUSE SET
| HGF30000 | 33KV 3Ph HG FUSE SETs | EA | 7004 |  |  | 7004
| HGF10002 | 11KV 3 Ph HG FUSE SETS | EA | 2492.6 | 1680 | 5100003052/6.1.16 | 2492.6
| HGF10003 | 11KV 1Ph HG FUSE SET WITHOUT INSULATORS | EA | 345.05 |  |  | 345.05
| HGF10004 | 11KV 1Ph HG FUSE SET WITH INSULATORS | EA | 381.1 |  |  | 381.1
| HGF00003 | LT HG FUSE SETS WITH OUT INSULATORS | EA | 1060.9 |  |  | 1060.9
| HGF00004 | LT 3 Ph HG FUSE SETS | EA | 1730.4 | 1150 | 5100002740/30.5.15 | 1730.4
| HGF00008 | LT 3PH HG FUSE SET WITH SCI | EA | 1166 |  |  | 1166
| HGF00006 | LT 1-PH HG FUSE SET | EA | 610.79 |  |  | 610.79
| HGF00007 | FUSE BASE WITH THROWOUT SWITCH 200A,500V | EA | 236.9 |  |  | 236.9
| HGF00010 | SUPPORTING INSULATORS FIXING CHANNEL | EA | 412 |  |  | 412
13) BATTERIES & CHARGERS
13.A) BATTERIES
| BAT00029 | 24V 40AH BATTERY WITH TRICKLE CHARGER | EA | 17000 | 16549.5 | 5100003026/15.12.15 | 17000
| BAT00025 | 24V 40AH BATTERY W/O CHARGER | EA | 5587.75 | 6795.7 | 5100003024/15.12.15 | 6795.7
| BAT00073 | 12V-180 AH Exide X press chgd battery | EA | 12617.5 |  |  | 12617.5
| BAT00064 | 12 V 150 AH BATTERY | EA | 11463.9 |  |  | 11463.9
| BAT00057 | 12V 130AH BATTERIES | EA | 9774.7 |  |  | 9774.7
| BAT00059 | 12V 100AH BATTERIES | EA | 8343 |  |  | 8343
| BAT00076 | 12V 100AH MAINTANANCE FREE BATTERY | EA | 7240.9 |  |  | 7240.9
| BAT00058 | 12V 99AH BATTERIES | EA | 6798 |  |  | 6798
| BAT00043 | 12V 88AH BATTERY | EA | 6658.95 |  |  | 6658.95
| BAT00051 | 12V 80AH MAINTENANCE FREE BATTERY | EA | 6386 |  |  | 6386
| BAT00016 | 12V 80AH LOW MAINT. LEAD ACID BATTERIES | EA | 6154.25 |  |  | 6154.25
| BAT00015 | 12V 80AH LEAD ACID BATTERIES | EA | 5999.75 |  |  | 5999.75
| BAT00074 | DIN 43AH- 12 V EXIDE MAINT FREE BATTERY | EA | 5943.1 |  |  | 5943.1
| BAT00056 | 12V 42AH MAINTENANCE FREE BATTERIES | EA | 5943.1 |  |  | 5943.1
| BAT00010 | 12V 40AH MAINTENANCE FREE BATTERIES | EA | 4223 |  |  | 4223
| BAT00075 | 12V 35AH MAINTANANCE FREE BATTERY | EA | 3821.3 |  |  | 3821.3
| BAT00042 | NS-40 12V.35AH BATTERIES | EA | 3749.2 |  |  | 3749.2
| BAT00050 | 12V 32AH BATTERY | EA | 3162.1 |  |  | 3162.1
| BAT00055 | 12V 26AH MAINTENANCE FREE BATTERIES | EA | 2811.9 |  |  | 2811.9
| BAT00068 | 12 V 22AH BATERY | EA | 2554.4 |  |  | 2554.4
| BAT00014 | 12V 7AH SMF BATTERY | EA | 849.75 |  |  | 849.75
| BAT00008 | 12V 21 PLATES CHARGED BATTERY | EA | 7853.75 |  |  | 7853.75
| BAT00005 | 12V 15 PLATES BATTERIES | EA | 7153.35 |  |  | 7153.35
| BAT00004 | 12V 13 PLATES BATTERIES | EA | 6097.6 |  |  | 6097.6
| BAT00045 | MHD-1500 EXIDE CHARGER BATTERIES | EA | 9125.8 |  |  | 9125.8
| BAT00044 | MHD-1300 EXIDE CHARGER BATTERIES | EA | 8796.2 |  |  | 8796.2
| BAT00046 | MM D - 99 TYPE EXIDE BATTERY | EA | 6787.7 |  |  | 6787.7
| BAT00062 | 26 AH BATTERY & INTERCONNECTING TERMINAL | SET | 7642.6 |  |  | 7642.6
| BAT00040 | BATTERIES STAND WITH ACCESSARIES | EA | 283.25 |  |  | 283.25
13.B) CHARGERS
| BAT00077 | 24V 100AH DUAL BATTERY CHARGER (Max 10A) | EA | 15012.25 |  |  | 15012.25
14) ENERGY METERS AND METERING EQUIPMENT
14.A) 220KV, 132 KV & 33KV HT TRIVECTOR METERS
| MHT30015 | HT TRIVECTOR 220KV/110V ELE METER 3 PH | EA | 16840.5 |  |  | 16840.5
| MHT30036 | HT TRIMETER 220KV/110V/100/1A 3 ELEMENT | EA | 16840.5 |  |  | 16840.5
| MHT30043 | HT TRIVECTOR 132KV/110V,100/1A RLY METER | EA | 16840.5 |  |  | 16840.5
| MHT30011 | HT TRIV MTR 132KV/110V100/1A15M IP CL0.2 | EA | 16840.5 |  |  | 16840.5
| MHT30052 | HT TVR MTR 132KV/110V 200/1A 15MIP 0.2S | EA | 16840.5 | 7559.99 | 5100002471/15.11.14 | 16840.5
| MHT30013 | HT TRIVECTOR 132KV/110V, 1A.METER" | EA | 16840.5 |  |  | 16840.5
| MHT30038 | HT TRIVECTOR 132KV/110V,100/1A TRACTION | EA | 16840.5 | 15871.75 | 5100002685/31.3.15 | 16840.5
| MHT30019 | HT TRVCTR MTR 33KV/110V 100/1A 30MI 0.2C | EA | 16480 |  |  | 16480
| MHT30004 | HT TRIVECTOR 33KV/110V 100/1A METERS | EA | 14337.6 |  |  | 14337.6
| MHT30021 | 33KV/110V100/1A TVR MTR 15M IP 0.2CL | EA | 14337.6 |  |  | 14337.6
| MHT30048 | HT TRIVECTOR METER 0.2 SPL CLASS (ABT) | EA | 19291.9 |  |  | 19291.9
| MHT30051 | HT TRVCTR MTR 33KV/110V 100/1A 15MI 0.2C | EA | 14049.2 |  |  | 14049.2
| MTO10033 | STATIC TRIMETER 33KV/110V/100/5A 30 MIN | EA | 14038.9 |  |  | 14038.9
| MHT30018 | HTTRIVECTOR 33KV/110V 200/1A METER,0.2CL | EA | 12802.9 | 7559.99 | 5100002702/23.4.15 | 12802.9
| MHT30008 | HTTRIVECTOR 33KV/110V200/1A MTR0.5C 30MI | EA | 12566 |  |  | 12566
| MHT30037 | HT STATIC TRIVECT METER 33KV/110V/60/5A | EA | 11227 |  |  | 11227
| MHT30005 | HT TRIVECTOR 33KV/110V 50/5A METERS | EA | 5325.1 |  |  | 5325.1
| MHT30049 | HT TRIVECT.METER 33KV /110V &200/1A 0.5S | EA | 4593.8 |  |  | 4593.8
| MHT30050 | HT TRIVECT.METER 33KV /110V & 50/1A 0.5S | EA | 4593.8 |  |  | 4593.8
| MHT30039 | HT TRI 33KV/110V 20/1A 30Min CL 0.5 Metr | EA | 4573.2 |  |  | 4573.2
| MHT30009 | HT TRVCTR MTR 33KV/110V 400/1A 30MI 0.2C | EA | 4552.6 |  |  | 4552.6
| MHT30047 | HT STATIC TRIVEC.33KV/110V 200/5A 0.5 CL | EA | 4552.6 |  |  | 4552.6
| MHT30044 | HT Trvctr Mtr 33KV/110V 400/1A 30MI 0.5C | EA | 4202.4 |  |  | 4202.4
| MTO10024 | MI AMMETER 0.5A | EA | 82.4 |  |  | 82.4
| MHT30057 | 132/110VHTTVR MT 100/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30060 | 132/110VHTTVR MT 50/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30062 | 132/110VHTTVR MT 200/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30058 | 33/110VHT TVR MT 50/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30061 | 33/110VHTTVR MT 25/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30064 | 33/110VHTTVR MT 200/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30065 | 33/110VHTTVR MT 100/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30059 | 11/110VHTTVR MT 100/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
| MHT30066 | 11/110VHTTVR MT 25/1A(AMR TOD & ABT) | EA | 66686 | 55000 | 5100001566/17.4.13 | 66686
14.B) 11KV HT TRIVECTOR METERS
| MHT10012 | HT TRIV MTR 11KV/110V 200/5A15M IP CL0.2 | EA | 4593.8 |  |  | 4593.8
| MHT30041 | HT TRIVECTOR 11KV/110V 200/5A METER | EA | 4593.8 |  |  | 4593.8
| MHT10042 | HT TRIVECT.METER 11KV /110V &200/5A 0.5S | EA | 4593.8 |  |  | 4593.8
| MHT10025 | HTTRIVECTOR 11KV/110V200/1A MTR0.2C 30MI | EA | 4593.8 |  |  | 4593.8
| MHT10019 | HTTRIVECTOR 11KV/110V200/1A MTR0.5C 30MI | EA | 4593.8 |  |  | 4593.8
| MHT10043 | HT TRIVECT.METER 11KV /110V &200/1A 0.5S | EA | 4593.8 |  |  | 4593.8
| MHT10010 | HT TRIVECTOR 11KV/110V 100/5A METERS | EA | 4593.8 |  |  | 4593.8
| MHT30022 | 11KV/110V 4W -30Min Int 100/5A Meter | EA | 4593.8 |  |  | 4593.8
| MHT10036 | HT TRIVECTOR METER CT RATIO 100/1A 30MIP | EA | 4593.8 |  |  | 4593.8
| MHT10009 | HT TRIVECTOR 11KV/110V 75/5A METERS | EA | 4593.8 |  |  | 4593.8
| MHT10008 | HT TRIVECTOR 11KV/110V 60/5A METERS | EA | 4593.8 |  |  | 4593.8
| MHT10007 | HT TRIVECTOR 11KV/110V 50/5A METERS | EA | 4593.8 |  |  | 4593.8
| MHT10033 | 3P4W 11KV/110V HT Trvctr Mtr 40/5A15M 0.2C | EA | 4593.8 |  |  | 4593.8
| MHT10006 | HT TRIV MTR 11KV/110V 40/5A 15M IP CL0.2 | EA | 4593.8 |  |  | 4593.8
| MHT10005 | HT TRIVEC 11KV/110V 20/5A METER CL 0.5 | EA | 4305.4 |  |  | 4305.4
| MHT10026 | HT TRIVECTOR 11KV/110V 20/5A ,ABB MAKE | EA | 4305.4 |  |  | 4305.4
| MHT10028 | HT Trvctr Mtr 11KV/110V 20/5A 30MIP 0.5C | EA | 4253.9 |  |  | 4253.9
| MHT10030 | HT TRIVECTOR METER 11KV/110V 20/5A | EA | 4593.8 |  |  | 4593.8
| MHT10041 | HT TRIVECT.METER 11KV /110V & 20/5A 0.5S | EA | 4593.8 |  |  | 4593.8
| MHT10038 | HT ST El'nic Mtr 11/110V 10/5A 0.5C | EA | 4181.8 |  |  | 4181.8
| MHT10024 | HT TRIVECTOR METER WITH PP BOX 10/5A | EA | 10609 |  |  | 10609
| MHT10003 | HT TRIVEC 11KV/110V 10/5A METERS CL 0.5 | EA | 4243.6 |  |  | 4243.6
| MHT10040 | HT TRIVECT.METER 11KV /110V & 10/5A 0.5S | EA | 4593.8 |  |  | 4593.8
| MHT30056 | HTTVRMTR11KV/110V10/5A30MIP 0.5S(RAPDRP) | EA | 5119.1 |  |  | 5119.1
| MHT30023 | HT STATIC TRIVECTOR METER Wth TTB 10/5A | EA | 7704.4 |  |  | 7704.4
| MHT30026 | HT TRIVECTOR METER 3X11 KV/110V /10/5A | EA | 4413.55 |  |  | 4413.55
| MHT10023 | HT METER BOXES | EA | 3738.9 | 2700 | 5100002795/23.6.15 | 3738.9
14.C) LT METERS
| MTO10023 | LT TRIVECTOR METER | EA | 3285.7 |  |  | 3285.7
| MTE30001 | 3 PH 10-40A ELECTRONI METER WITH PP BOX | EA | 1890.05 |  |  | 1890.05
| MTE30014 | 3PH 10-40A ESE METER(STEP MOTOR)W/O PPBX | EA | 1452.3 |  |  | 1452.3
| MTE30011 | 3PH 10-40A CONT TY METER W/O PP BOX | EA | 947.6 |  |  | 947.6
| MTM30009 | 3 PH 5A ELE MECH METERS | EA | 659.2 |  |  | 659.2
| MTM30012 | 3 PH 50A ELE MECH METERS | EA | 659.2 |  |  | 659.2
| MTM10001 | 1 PH 2.5-10A ELE MECH METER | EA | 999.1 |  |  | 999.1
| MTM10003 | 1 PH 2.5-10A ELE MECHANICAL METER-SICK | EA | 999.1 |  |  | 999.1
| MTE10015 | 1PH 5-20A COUNTER TYPE METER WITH PP BOX | EA | 350.2 |  |  | 350.2
| MTE10018 | 1PH 5-30A ELECTRO STATIC ENERGY METERS | EA | 947.6 | 738 | 5100003066/20.1.16 | 947.6
| MTM10006 | 1 PH 5-20A ELE MECHANICAL METER | EA | 751.9 |  |  | 751.9
| MTE10014 | 1 PH 5-20A ELE METER WITH PP BOX | EA | 458.35 |  |  | 458.35
14.D) CT OPERATED METERS
| MCT30015 | 3PH 200/5A LTCT OPERATED ELE METER CL1.0 | EA | 7725 |  |  | 7725
| MCT30020 | 3PH 4W LT/CT OPTD TRI MTR CLAS 1.00 | EA | 7725 |  |  | 7725
| MCT30007 | 3PH 200/5A LT CT OPERTD TVR METER CL 0.5 | EA | 7725 | 6075 | 5100002986/9.10.15 | 7725
| MCT30004 | 3PH 125/5A LT CT OPERTD TVR METER CL 0.5 | EA | 7210 | 6839 | 5100002280/16.6.14 | 7210
| MCT30039 | 3PH4W200/5A LTCTOPTVR MTR CL0.5S(RAPDRP) | EA | 6921.6 | 6543.51 | 5100002091/7.2.14 | 6921.6
| MCT30014 | 3Ø 4W CT OPERATEDMETER WITH PPBOX 125/5A | EA | 7328.45 | 5599.83 | 5100002359/7.8.14 | 7328.45
| MCT30038 | 3P 4W CT OP ELTRI MT125/5A PPB 0.5S W CT | EA | 7261.5 | 5650 | 5100002942/31.8.15 | 7261.5
| MCT30016 | 3P 4W CT OP EL TRIV MTR 0.5 125/5A PP BX | EA | 5979.15 |  |  | 5979.15
| MCT30037 | 3P 4W CT OP EL TRIV MT 125/5A CL 0.5S | EA | 7044.17 |  |  | 7044.17
| MCT30011 | 3 PH LT CT OPERATED OBSOLETE METER | EA | 1524.4 |  |  | 1524.4
| MCT30012 | 3 PH LT MD INDICATORS OBSOLETE | EA | 1828.25 |  |  | 1828.25
| MCT30017 | 3Ph LT/CT OPERATED METERS /5 A Tested | EA | 782.8 |  |  | 782.8
| MCT30030 | ASSEMBLED CT METER BOX WITH LT CT 125/5A | EA | 4243.6 |  |  | 4243.6
| MCT30031 | ASSEMBLED CT METER BOX WITH LT CT 100/5A | EA | 4243.6 |  |  | 4243.6
| MCT30029 | ASSEMBLED CT METER BOX WITH LT CT 50/5A | EA | 4243.6 | 6839 | 5100002281/16.6.14 | 6839
| MCT30032 | LTCT METER BOX W 1 CT METER&3 200/5A CTS | EA | 4068.5 | 6010 | 5100003084/17.2.16 | 6010
| MCT30028 | LTCT METER BOX W 1 CT METER&3 125/5A CTS | EA | 3378.4 | 1998.08 | 5100002948/31.8.15 | 3378.4
| MCT30027 | LTCT METER BOX W1LTCT METER&3 100/5A CTS | EA | 2652.25 |  |  | 2652.25
| MCT30026 | LTCT METER BOX W1LTCT METER&3 50/5A CTS | EA | 1390.5 |  |  | 1390.5
| MCT30035 | RIGGED UP 1PH SMC METER BOX LT CTs 50/5A | EA | 1390.5 |  |  | 1390.5
| MCT30022 | CT OPERATD 11KV/110V 200/5A 4WIRE E.M | EA | 0 |  |  | 0
| MCT30024 | 1PH 15/5A CT METER WITH BOX | EA | 1709.8 |  |  | 1709.8
14.E) LT CURRENT TRANSFORMER
| ITR00015 | LT CT'S 200/5A FOR LT TRIVECTOR METERS | EA | 381.1 |  |  | 381.1
| ITR00013 | LT CT'S 200/5A | EA | 381.1 |  |  | 381.1
| ITR00012 | LT CT'S 125/5A | EA | 412 |  |  | 412
| ITR00011 | LT CT'S 100/5A | EA | 535.6 |  |  | 535.6
| ITR00014 | LT CT'S 50/5A | EA | 540.75 |  |  | 540.75
15) BOXES
| BXS00041 | HT METER BOX | EA | 4120 | 2700 | 510002794/23.06.15 | 4120
| BXS00011 | A TY(SPL) DIST. BOX WITH 200A,500V FUSE | EA | 5562 | 6960 | 5100002825/14.7.15 | 6960
| BXS00146 | LT DISTR. BOX 3X2X1 ATYPE SPL.DIST.BOXES | EA | 3502 |  |  | 3502
| BXS00010 | A TYPE BOX | EA | 3090 |  |  | 3090
| BXS00001 | 3 PHASE CT METER BOXES (EMPTY) | EA | 1957 |  |  | 1957
| BXS00172 | 3 PHASE SPECIAL TYPE METER BOXES | EA | 530.45 |  |  | 530.45
| BXS00170 | SMC 3 PHASE METER BOXES | EA | 473.8 |  |  | 473.8
| BXS00147 | LT METER BOX | EA | 432.6 |  |  | 432.6
| BXS00171 | SMC METER BOX FOR HOUSING 1-PH METER &CT | EA | 381.1 |  |  | 381.1
| BXS00174 | SMC DISTRIBUTION BOX | EA |  | 13300 | 5100003094/08.03.16 | 13300
16) EARTHING MATERIALS
| EMT00006 | CI EARTH PIPE 80 MM DIA 2.5MTS LENGTH | EA | 2470.97 | 2170 | 5100003030/22.12.15 | 2470.97
| EMT00022 | GI EARTH PIPE 40 MM 2.5 MTS LONG | EA | 592 | 479 | 5100002847/23.7.15 | 592
| EMT00018 | GI EARTH FLAT 25 MM X 4 MM | KG | 25.75 |  |  | 25.75
17) OTHER MATERIALS
| OTH00057 | A.C. DISTRIBUTION PANELS | EA | 29174.75 |  |  | 29174.75
| OTH00126 | DC ANNUNCIATION PANEL | EA | 12360 |  |  | 12360
| CAH00060 | HAND HELD COMPUTER FOR SPOT BILLING | EA | 13081 | 10000 | 5100002760/1.9.15 | 13081
| OMT10030 | CMRI WITH ACCESSORIES | EA | 31621 |  |  | 31621
| FBE00027 | LT OPEN WIRING FUSE SET STRUCTURE | EA | 751.9 |  |  | 751.9

## REC Const. Std(P15-44)
Costdata per Km of 33 KV Line (Single Circuit) with 100 Sq.mm AAA Conductor over 11.0Mts.
Spun/PSCC Poles at 60 Mts. Span
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs. | Labour
1 | PLS00007 | 11.0 mts PSCC Spun Pole | 18 | 11300 | Each | 203400 | 70038
2 | FBE30004 | 33KV V cross arms without clamps | 16 | 1026 | Each | 16416 | 1728
3 | FBE30006 | 33 KV Top Cleat with clamps | 16 | 519 | Each | 8304 | 800
4 | FBE00026 | 33KV Tapping Channel "X" Arms | 4 | 1112 | Each | 4448 | 432
5 | FBE00034 | 33KV MS Back Clamps for spun poles | 20 | 162 | Each | 3240
6 | FBE30010 | 33 KV MS Stay sets without clamps | 8 | 525 | Each | 4200 | 2088 | 1848 | 3936
7 | FBE30002 | 33KV MS stay clamps | 8 | 218 | Set | 1744
8 | CDR00004 | 100 Sq.mm AAA Conductor | 3.06 | 50953 | K.M. | 155916 | 17325.72
9 | INS30001 | 33 KV Pin - Insulator | 51 | 387 | Each | 19737 | 2091
10 | HWR00003 | 33 KV GI Pin | 51 | 163 | Each | 8313
11 | INS30004 | 33KV Polymer Insulator | 12 | 649 | Each | 7788 | 852
12 | HWR00004 | 33KV Metal Parts | 12 | 180 | Set | 2160 | 95354.72
13 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 17630
14 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 3516
|  | Total Cost of Material |  |  |  | 456812 | 21752.9524
[8 empty] | 435059.0476 | 4350.5905
|  | 3% storage & handling charges on items (1) to (12) |  | 435666 |  | 13070
|  | 3% Contingencies on Materials |  |  |  | 13704
|  | Labour & Transport |  |  |  | 95355
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 11785.878
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 953.55
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 4247
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 45681.2
[5 empty] | Total | 641608.628
Costdata per Km of 33 KV Line with 100 Sq.mm AAA Conductor over 9.1 Mts.
Costdata per Km of 33 KV Line (Single Circuit) with 100 Sq.mm AAA Conductor over 12.5Mts.
Spun Poles at 60 Mts. Span
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs. | labour
1 | PLS00014 | 12.5 mts PSCC Spun Pole | 18 | 12200 | Each | 219600 | 92538
2 | FBE30004 | 33KV V cross arms without clamps | 16 | 1026 | Each | 16416 | 1728
3 | FBE30006 | 33 KV Top Cleat with clamps | 16 | 519 | Each | 8304 | 800
4 | FBE00026 | 33KV Tapping Channel "X" Arms | 4 | 1112 | Each | 4448 | 432
5 | FBE00034 | 33KV MS Back Clamps for spun poles | 20 | 162 | Each | 3240
6 | FBE30010 | 33 KV MS Stay sets without clamps | 8 | 525 | Each | 4200 | 2088
7 | FBE30002 | 33KV MS stay clamps | 8 | 218 | Set | 1744
8 | CDR00004 | 100 Sq.mm AAA Conductor | 3.06 | 50953 | K.M. | 155916 | 17325.72
9 | INS30001 | 33 KV Pin - Insulator | 51 | 387 | Each | 19737 | 2091
10 | HWR00003 | 33 KV GI Pin | 51 | 163 | Each | 8313
11 | INS30004 | 33KV Polymer Insulator | 12 | 649 | Each | 7788 | 852
12 | HWR00004 | 33KV Metal Parts | 12 | 180 | Set | 2160 | 117854.72
13 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 17630
14 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 3516
|  | Total Cost of Material |  |  |  | 473012 | 22524.381
450487.619
|  | 3% storage & handling charges on items (1) to (12) |  | 451866 |  | 13556
|  | 3% Contingencies on Materials |  |  |  | 14190
|  | Labour & Transport |  |  |  | 117855
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 14566.878
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 1178.55
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 4419
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 47301.2
[5 empty] | Total | 686078.628
Costdata per Km of 33 KV Line (Double Circuit) with 100 Sq.mm AAA Conductor over 12.5Mts.
PSCC Poles at 60 Mts. Span
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs. | Labour
1 | PLS00014 | 12.5 mts PSCC Spun Pole | 18 | 12200 | Each | 219600 | 92538
2 | PLS00004 | 9.1mts PSCC Poles for strut | 8 | 3640 | Each | 29120 | 15344
3 | FBE30004 | 33KV V cross arms without clamps | 45 | 1026 | Each | 46170 | 4860
4 | FBE00026 | 33KV Tapping Channel "X" Arms | 12 | 1112 | Each | 13344 | 1296 |  |  |  | 16.6667
5 | FBE00034 | 33KV MS Back Clamps for spun poles | 57 | 162 | Each | 9234
6 | CDR00004 | 100 Sq.mm AAA Conductor | 6.12 | 50953 | K.M. | 311832 | 34651.44
7 | INS30001 | 33 KV Pin - Insulator | 96 | 387 | Each | 37152 | 3936
8 | HWR00003 | 33 KV GI Pin | 96 | 163 | Each | 15648
9 | INS30004 | 33KV Polymer Insulator | 24 | 649 | Each | 15576 | 1704
10 | HWR00004 | 33KV Metal Parts | 24 | 180 | Set | 4320
11 | FBG00019 | MS Stay Clamps for Strut | 16 | 72 | Each | 1152 | 154329.44
12 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 17630
13 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 3516
|  | Total Cost of Material |  |  |  | 724294 | 34490.1905
689803.8095
|  | 3% storage & handling charges on items (1) to (11) |  | 703148 |  | 21094
|  | 3% Contingencies on Materials |  |  |  | 21729
|  | Labour & Transport |  |  |  | 154330
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 19075.188
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 1543.3
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 6821
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 72429.4
[5 empty] | Total | 1021315.888
[5 empty] | or say | 1021300
Costdata per Km of 33 KV Line with 100 Sq.mm AAA Conductor over 9.1 Mts.
PSCC Poles at 40 Mts. Span in Urban Areas.
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs. | LABOUR | pit
1 | PLS00004 | 9.1 mts PSCC Pole | 27 | 3640 | Each | 98280 | 51786 | 4617
2 | FBE30003 | 33KV V cross arms with clamps | 24 | 1197 | Each | 28728 | 2592
3 | FBE30006 | 33 KV Top Cleat with clamps | 24 | 519 | Each | 12456 | 1224
4 | FBE00026 | 33KV Tapping Channel "X" Arms | 4 | 1112 | Each | 4448 | 432
5 | FBE30001 | 33KV MS Back Clamps | 4 | 139 | Each | 556
6 | FBE30010 | 33 KV MS Stay sets without clamps | 8 | 525 | Each | 4200 | 2088 | 1368
7 | FBE30002 | 33KV MS stay clamps | 8 | 218 | Set | 1744 | 1680
8 | CDR00004 | 100 Sq.mm AAA Conductor | 3.06 | 50953 | K.M. | 155916 | 17325.72
9 | INS30001 | 33 KV Pin - Insulator | 75 | 387 | Each | 29025 | 3075
10 | HWR00003 | 33 KV GI Pin | 75 | 163 | Each | 12225
11 | INS30004 | 33KV Polymer Insulator | 12 | 649 | Each | 7788 | 852
12 | HWR00004 | 33KV Metal Parts | 12 | 180 | Set | 2160
13 | MST00012 | 100 x 50 MS Channel for DP Structure (CP) | 150 | 54 | Kg | 8100 | 452
14 | MST00002 | MS Angle 50 x 50 x 6 for DP Structure (CP) | 80 | 54 | Kg | 4320 | 81506.72
15 | WRS00005 | GI wire No.8 | 20 | 63 | Kg | 1260
16 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 15630
17 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 3516
|  | Total Cost of Material |  |  |  | 390352 | 18588.1905
371763.8095
|  | 3% storage & handling charges on items (1) to (15) |  | 371206 |  | 11136
|  | 3% Contingencies on Materials |  |  |  | 11711
|  | Labour & Transport |  |  |  | 81507
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 10074.2652
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 815.07
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 3702
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 39035.2
[5 empty] | Total | 548332.5352
[5 empty] | or say | 548300
Costdata per Km of 33 KV Line with 100 Sq.mm AAA Conductor over 9.1 Mts.
PSCC Poles at 60 Mts. Span in Rural Areas.
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs. | Labour
1 | PLS00004 | 9.1mts PSCC Pole | 19 | 3640 | Each | 69160 | 36442 | 3249
2 | FBE30003 | 33KV V cross arms with clamps | 16 | 1197 | Each | 19152 | 1728
3 | FBE30006 | 33 KV Top Cleat with clamps | 16 | 519 | Each | 8304 | 800
4 | FBE00026 | 33KV Tapping Channel "X" Arms | 4 | 1112 | Each | 4448 | 432
5 | FBE30001 | 33KV MS Back Clamps | 4 | 139 | Each | 556
6 | FBE30010 | 33 KV MS Stay sets without clamps | 8 | 525 | Each | 4200 | 2088
7 | FBE30002 | 33KV MS stay clamps | 8 | 218 | Set | 1744 | 1680
8 | CDR00004 | 100 Sq.mm AAA Conductor | 3.06 | 50953 | K.M. | 155916.18 | 17325.72
9 | INS30001 | 33 KV Pin - Insulator | 51 | 387 | Each | 19737 | 2091
10 | HWR00003 | 33KV GI Pin | 51 | 163 | Each | 8313
11 | INS30004 | 33KV Polymer Insulator | 12 | 649 | Each | 7788 | 852
12 | HWR00004 | 33KV Metal Parts | 12 | 180 | Set | 2160
13 | MST00012 | 100 x 50 MS Channel for DP Structure (CP) | 150 | 54 | Kg | 8100 | 452
14 | MST00002 | MS Angle 50 x 50 x 6 for DP Structure (CP) | 80 | 54 | Kg | 4320 | 63890.72
15 | WRS00005 | GI wire No.8 | 20 | 63 | Kg | 1260
16 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 15630
17 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 3516
|  | Total Cost of Material |  |  |  | 334304.18 | 15919.2467
318384.9333
|  | 3% storage & handling charges on items (1) to (15) |  | 315158.18 |  | 9455
|  | 3% Contingencies on Materials |  |  |  | 10029
|  | Labour & Transport |  |  |  | 63891
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 7896.9276
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 638.91
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 3173
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 33430.418
[5 empty] | Total | 462818.4356
[5 empty] | or say | 462800
Costdata per Km of 11 KV Line with 100 Sq.mm AAA Conductor over 9.1Mts.
PSCC Poles at 40 Mts. Span in Urban Areas.
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00004 | 9.1mts PSCC Pole | 27 | 3640 | Each | 98280 | 51786
2 | FBE10028 | 11KV Angle V-X Arm With Clamp 140 KG | 23 | 533 | Each | 12259 | 1472
3 | FBE10007 | 11KV Top Cleat with Clamps | 23 | 281 | Each | 6463 | 897
4 | FBE10004 | 11KV MS Channel "X" Arms (Tapping) 75 x 40 | 4 | 545 | Each | 2180 | 256
5 | FBE00002 | 11KV MS back clamps for 9.1mts PSCC Poles | 4 | 100 | Each | 400 | 1576
6 | FBE10022 | Stay sets with clamps | 8 | 448 | Each | 3584 | 2088 | 1576
7 | CDR00004 | 100 Sq.mm AAA Conductor | 3.06 | 50953 | K.M. | 155916 | 17325.72
8 | INS10001 | 11 KV Pin - Insulator | 72 | 54 | Each | 3888 | 1872
9 | HWR00001 | 11KV GI Pin | 72 | 59 | Each | 4248
10 | INS10003 | 11KV polymer insulators (C&T) | 12 | 196 | Each | 2352 | 372
11 | HWR00002 | 11KV metal parts (C&T) | 12 | 82 | Set | 984
12 | MST00012 | 100 x 50 MS Channel for DP Structure (CP) | 120 | 54 | Kg | 6480
13 | MST00002 | MS Angle 50 x 50 x 6 for DP Structure (CP) | 60 | 54 | Kg | 3240 | 452
14 | WRS00005 | GI wire No.8 | 20 | 63 | Kg | 1260 | 78096.72
15 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 16322
16 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 4040
|  | Total Cost of Material |  |  |  | 321896 | 15328.381
306567.619
|  | 3% storage & handling charges on items (1) to (14) |  | 301534 |  | 9046
|  | 3% Contingencies on Materials |  |  |  | 9657
|  | Labour & Transport |  |  |  | 78097
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 9652.7892
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 780.97
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 3055
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 32189.6
[5 empty] | Total | 464374.3592
[5 empty] | or say | 464400
Costdata per Km of 11 KV Line with 55 Sq.mm AAA Conductor over 9.1Mts.
PSCC Poles at 60 Mts. Span in Rural areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00004 | 9.1mts PSCC Pole | 18 | 3640 | Each | 65520 | 34524 | 3078
2 | FBE10034 | 11KV Angle V-X Arm With Clamp200 KG | 15 | 533 | Each | 7995 | 960
3 | FBE10007 | Top Clamp with cleat | 15 | 281 | Each | 4215 | 585
4 | FBE10004 | 11KV MS Channel "X" Arms (Tapping) 75 x 40 | 4 | 545 | Each | 2180 | 256
5 | FBE00002 | 11KV MS back clamps for 9.1mts PSCC Poles | 4 | 100 | Each | 400 | 1576
6 | FBE10022 | Stay sets with clamps | 8 | 448 | Each | 3584 | 2088 | 1368
7 | CDR00003 | 55 Sq.mm AAA Conductor | 3.06 | 29490 | K.M. | 90239 | 9476.82
8 | INS10001 | 11 KV Pin - Insulator | 48 | 54 | Each | 2592 | 1248
9 | HWR00001 | 11KV GI Pin | 48 | 59 | Each | 2832
10 | INS10003 | 11KV polymer insulators (C&T) | 12 | 196 | Each | 2352 | 372
11 | HWR00002 | 11KV metal parts (C&T) | 12 | 82 | Set | 984
12 | MST00012 | 100 x 50 MS Channel for DP Structure (CP) | 120 | 54 | Kg | 6480
13 | MST00002 | MS Angle 50 x 50 x 6 for DP Structure (CP) | 60 | 54 | Kg | 3240 | 452
14 | WRS00005 | GI wire No.8 | 20 | 63 | Kg | 1260 | 51537.82 | 4446
15 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 16322
16 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 4040
|  | Total Cost of Material |  |  |  | 214235 | 10201.6667
|  | 3% storage & handling charges on items (1) to (14) |  | 193873 |  | 5816 | 204033.3333
|  | 3% Contingencies on Materials |  |  |  | 6427
|  | Labour & Transport |  |  |  | 51538
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 6370.0968
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 515.38
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 2033
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 21423.5
[5 empty] | Total | 308357.9768
[5 empty] | or say | 308400
Costdata per Km of 11 KV Line with 55 Sq.mm AAA Conductor over 8 .0Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 22 | 1875 | Each | 41250 | 25828
2 | FBE10028 | 11KV Angle V-X Arm With Clamp 140 KG | 18 | 533 | Each | 9594 | 1152
3 | FBE10007 | Top Clamp with cleat | 18 | 281 | Each | 5058 | 702
4 | FBE10004 | 11KV MS Channel "X" Arms (Tapping) 75 x 40 | 4 | 545 | Each | 2180 | 256
5 | FBE00002 | 11KV MS back clamps for 9.1mts PSCC Poles | 4 | 100 | Each | 400 | 1680
6 | FBE10022 | Stay sets with clamps | 8 | 448 | Each | 3584 | 2088
7 | CDR00003 | 55 Sq.mm AAA Conductor | 3.06 | 29490 | K.M. | 90239 | 9476.82
8 | INS10001 | 11 KV Pin - Insulator | 57 | 54 | Each | 3078 | 1248
9 | HWR00001 | 11KV GI Pin | 57 | 59 | Each | 3363
10 | INS10003 | 11KV polymer insulators (C&T) | 12 | 196 | Each | 2352 | 372
11 | HWR00002 | 11KV metal parts (C&T) | 12 | 82 | Set | 984
12 | MST00012 | 100 x 50 MS Channel for DP Structure (CP) | 120 | 54 | Kg | 6480
13 | MST00002 | MS Angle 50 x 50 x 6 for DP Structure (CP) | 60 | 54 | Kg | 3240 | 452
14 | WRS00005 | GI wire No.8 | 20 | 63 | Kg | 1260 | 43254.82
15 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 16322
16 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 4040
|  | Total Cost of Material |  |  |  | 193424 | 9210.6667
184213.3333
|  | 3% storage & handling charges on items (1) to (14) |  | 173062 |  | 5192
|  | 3% Contingencies on Materials |  |  |  | 5803
|  | Labour & Transport |  |  |  | 43252
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5345.9472
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 432.52
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1842
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 19342.4
[5 empty] | Total | 274633.8672
[5 empty] | or say | 274600
Costdata per Km of 11 KV Line with 55 Sq.mm AAA Conductor over 8.0 Mts.
PSCC Poles (200Kgs) at 50 Mts. Span in Rural Areas.
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00002 | 8.0mts PSCC Pole | 22 | 1995 | Each | 43890 | 25828
2 | FBE10034 | 11KV Angle V-X Arm With Clamp200 KG | 18 | 533 | Each | 9594 | 1152
3 | FBE10007 | Top Clamp with cleat | 18 | 281 | Each | 5058 | 702
4 | FBE10004 | 11KV MS Channel "X" Arms (Tapping) 75 x 40 | 4 | 545 | Each | 2180 | 256
5 | FBE00002 | 11KV MS back clamps for 9.1mts PSCC Poles | 4 | 100 | Each | 400 | 1680
6 | FBE10022 | Stay sets with clamps | 8 | 448 | Each | 3584 | 2088
7 | CDR00003 | 55 Sq.mm AAA Conductor | 3.06 | 29490 | K.M. | 90239 | 9476.82
8 | INS10001 | 11 KV Pin - Insulator | 57 | 54 | Each | 3078 | 1482
9 | HWR00001 | 11KV GI Pin | 57 | 59 | Each | 3363
10 | INS10003 | 11KV polymer insulators (C&T) | 12 | 196 | Each | 2352 | 372
11 | HWR00002 | 11KV metal parts (C&T) | 12 | 82 | Set | 984
12 | MST00012 | 100 x 50 MS Channel for DP Structure (CP) | 120 | 54 | Kg | 6480
13 | MST00002 | MS Angle 50 x 50 x 6 for DP Structure (CP) | 60 | 54 | Kg | 3240 | 452
14 | WRS00005 | GI wire No.8 | 20 | 63 | Kg | 1260 | 43488.82
15 |  | Concreting of Pole, Stay sets & Base concreting | LS |  | LS | 16322
16 |  | Misc. Items like coil earthing, pipe earthing, danger-boards, bolts & nuts, etc. | LS |  | LS | 4040
|  | Total Cost of Material |  |  |  | 196064 | 9336.381
|  | 3% storage & handling charges on items (1) to (14) |  | 175702 |  | 5271 | 186727.619
|  | 3% Contingencies on Materials |  |  |  | 5882
|  | Labour & Transport |  |  |  | 43489
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5375.2404
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 434.89
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1864
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 19606.4
[5 empty] | Total | 277986.5304
[5 empty] | or say | 278000
Costdata per Km of 6.3 KV S-ph Line with 55 Sq.mm AAA Conductor over 9.1 Mts.
PSCC Poles at 50 Mts. Span in Urban Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00004 | 9.1mts PSCC Pole | 21 | 3640 | Each | 76440 | 40278
2 | FBE10007 | Top Clamp with cleat | 19 | 281 | Each | 5339 | 741
3 | FBE00033 | LT S-ph 2W cross arms without clamp | 21 | 268 | Each | 5628 | 966
4 | FBE00041 | MS Back Clamp | 21 | 72 | Each | 1512 | 1260
5 | FBE10022 | Stay sets | 6 | 448 | Each | 2688 | 1566
6 | CDR00003 | 55 Sq.mm AAA Conductor | 2.04 | 29490 | K.M. | 60159.6 | 6317.88
7 | INS10001 | 11 KV Pin - Insulator | 20 | 54 | Each | 1080 | 520
8 | HWR00001 | 11KV GI Pin | 20 | 59 | Each | 1180
9 | INS00001 | LT Pin Isulator | 19 | 14 | Each | 266 | 494
10 | HWR00015 | LT GI Pins | 19 | 29 | Each | 551
11 | INS00002 | LT Shackles | 4 | 12 | Each | 48 | 104
12 | HWR00016 | LT metal parts | 4 | 32 | Set | 128
13 | INS10003 | 11KV polymer insulators (C&T) | 4 | 196 | Each | 784 | 124
14 | HWR00002 | 11KV metal parts (C&T) | 4 | 82 | Set | 328 | 52370.88
15 |  | Concreting of Pole,Stay sets & Base concreting | LS |  | L.S. | 16322
16 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts | LS |  | L.S. | 2257
& nuts, etc.
|  | Total Cost of Material |  |  |  | 174710.6 | 8319.5524
166391.0476
|  | 3% storage & handling charges on items (1) to (14) |  | 79691.6 |  | 2390.748
|  | 3% Contingencies on Materials |  |  |  | 5241.318
|  | Labour & Transport |  |  |  | 52371
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 6473.0556
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 523.71
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1655
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 17471.06
[5 empty] | Total | 260836.4916
[5 empty] | or say | 260800 | 49895.5617
Costdata per Km of 6.3 KV S-ph Line with 55 Sq.mm AAA Conductor over 8.0 Mts.
PSCC Poles (140Kgs) at 60 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00002 | 8.0 mts PSCC Pole | 18 | 1875 | Each | 33750 | 21132
2 | FBE10007 | Top Clamp with cleat | 16 | 281 | Each | 4496 | 624
3 | FBE00033 | LT S-ph 2W cross arms without clamp | 18 | 268 | Each | 4824 | 828
4 | FBE00041 | MS Back Clamp | 18 | 72 | Each | 1296 | 1260
5 | FBE10022 | Stay sets | 6 | 448 | Set | 2688 | 1566
6 | CDR00003 | 55 Sq.mm AAA Conductor | 2.04 | 29490 | K.M. | 60159.6 | 6317.88
7 | INS10001 | 11 KV Pin - Insulator | 16 | 54 | Each | 864 | 416
8 | HWR00001 | 11KV GI Pin | 16 | 59 | Each | 944
9 | INS00001 | LT Pin Isulator | 16 | 14 | Each | 224 | 416
10 | HWR00015 | LT GI Pins | 16 | 29 | Each | 464
11 | INS00002 | LT Shackles | 4 | 12 | Each | 48 | 104
12 | HWR00016 | LT metal parts | 4 | 32 | Set | 128
13 | INS10003 | 11KV polymer insulators (C&T) | 4 | 196 | Each | 784 | 124
14 | HWR00002 | 11KV metal parts (C&T) | 4 | 82 | Set | 328 | 32787.88
15 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  | Ls | L.S. | 16322
16 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  | Ls | L.S. | 2257
& nuts, etc.
|  | Total Cost of Material |  |  |  | 129576.6 | 6170.3143
123406.2857
|  | 3% storage & handling charges on items (1) to (14) |  | 110997.6 |  | 3329.928
|  | 3% Contingencies on Materials |  |  |  | 3887.298
|  | Labour & Transport |  |  |  | 32788
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4052.5968
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 327.88
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1233
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 12957.66
[5 empty] | Total | 188152.9628
[5 empty] | or say | 188200
Costdata per Km of LT 3-Ph 5 Wire Line(Horizontal formation ) with
4 x 55 Sq.mm + 1 x 34 Sq.mm AAAC
over 8.0 Mts. PSCC Poles (200Kgs) at 40 Mts in Urban areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00002 | 8.0 mts PSCC Pole (2 poles for strut) | 28 | 1995 | Each | 55860 | 32872
2 | FBE00008 | L.T. 3 Phase 5W cross arms | 26 | 381 | Each | 9906 | 1196
3 | FBE00001 | Back Clamp | 26 | 72 | Each | 1872
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00003 | 55 Sq.mm AAA Conductor | 4.08 | 29490 | K.M. | 120319.2 | 12635.76
6 | CDR00002 | 34 Sq.mm AAA Conductor | 1.02 | 17685 | K.M. | 18038.7 | 1987.98
7 | INS00002 | LT Shackles | 20 | 12 | Each | 240 | 520
8 | HWR00016 | LT metal parts | 20 | 32 | Set | 640
9 | INS00001 | LT Pin Isulator | 96 | 14 | Each | 1344 | 2496
10 | HWR00015 | LT GI Pins | 96 | 29 | Each | 2784 | 52751.74
11 | FBE00048 | MS Strut Clamps for 8.0mts (Set) | 2 | 77 | Each | 154
12 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 16322
13 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 231969.9 | 11046.1857
220923.7143
|  | 3% storage & handling charges on items (1) to (11) |  | 212433.9 |  | 6373.017
|  | 3% Contingencies on Materials |  |  |  | 6959.097
|  | Labour & Transport |  |  |  | 52753
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 6520.2708
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 527.53
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 2202
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 23196.99
[5 empty] | Total | 330501.8048
[5 empty] | or say | 330500
Costdata per Km of LT 3-Ph 5 Wire Line(Horizontal formation ) with
3 x 55 Sq.mm + 2 x 34 Sq.mm AAAC over 8.0Mts.
PSCC Poles (200Kgs) at 50 Mts. Span in Rural Areas (MHQs & Major Panchayath)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00002 | 8.0mts PSCC Pole | 21 | 1995 | Each | 41895 | 24654
2 | FBE00008 | L.T. 3 Phase 5W cross arms | 21 | 381 | Each | 8001 | 966
3 | FBE00001 | Back Clamp | 21 | 72 | Each | 1512
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00003 | 55 Sq.mm AAA Conductor | 3.06 | 29490 | K.M. | 90239.4 | 9476.82
6 | CDR00002 | 34 Sq.mm AAA Conductor | 2.04 | 17685 | K.M. | 36077.4 | 3975.96
7 | INS00002 | LT Shackles | 20 | 12 | Each | 240 | 520
8 | HWR00016 | LT metal parts | 20 | 32 | Set | 640
9 | INS00001 | LT Pin Isulator | 76 | 14 | Each | 1064 | 1976
10 | HWR00015 | LT GI Pins | 76 | 29 | Each | 2204 | 42612.78
11 |  | Concreting of Pole,Stay sets & |  |  | L.S. | 16322
Base concreting
12 |  | Misc. Items like coil earthing, |  |  | L.S. | 3214
pipe earthings, danger-boards, bolts
& nuts, etc.
|  | Total Cost of Material |  |  |  | 202684.8 | 9651.6571
193033.1429
|  | 3% storage & handling charges on items (1) to (10) |  | 183148.8 |  | 5494.464
|  | 3% Contingencies on Materials |  |  |  | 6080.544
|  | Labour & Transport |  |  |  | 42613
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5266.9668
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 426.13
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1925
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 20268.48
[5 empty] | Total | 284759.3848
[5 empty] | or say | 284800
Costdata per Km of LT 3-Ph 5 Wire Line(Horizontal formation ) with
5 x 34 Sq.mm AAAC over 8.0 Mts.
PSCC Poles (200Kgs) at 50 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00002 | 8.0mts PSCC Pole | 21 | 1995 | Each | 41895 | 24654
2 | FBE00008 | L.T. 3 Phase 5W cross arms | 21 | 381 | Each | 8001 | 966
3 | FBE00001 | Back Clamp | 21 | 72 | Each | 1512
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00002 | 34 Sq.mm AAA Conductor | 5.1 | 17685 | K.M. | 90193.5 | 9939.9
6 | INS00002 | LT Shackles | 20 | 12 | Each | 240
7 | HWR00016 | LT metal parts | 20 | 32 | Set | 640 | 520
8 | INS00001 | LT Pin Isulator | 76 | 14 | Each | 1064 | 1216
9 | HWR00015 | LT GI Pins | 76 | 29 | Each | 2204
10 |  | Concreting of Pole,Stay sets & |  |  |  |  | 38339.9
|  | Base concreting | L.S. |  | L.S. | 16322
11 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts | L.S. |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 166561.5 | 7931.5
158630
|  | 3% storage & handling charges on items (1) to (9) |  | 147025.5 |  | 4410.765
|  | 3% Contingencies on Materials |  |  |  | 4996.845
|  | Labour & Transport |  |  |  | 38340
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4738.824
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 383.4
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1581
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 16656.15
[5 empty] | Total | 237668.484
[5 empty] | or say | 237700
Costdata per Km of LT 3-Ph 5 Wire Line(Horizontal formation ) with
4 x 55 Sq.mm + 1 x 34 Sq.mm AAAC
over 8.0 Mts. PSCC Poles (140Kgs) at 40 Mts in Urban areas (Corporation & Municipalities)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs. | Labour
1 | PLS00001 | 8.0 mts PSCC Pole (2 poles for strut) | 28 | 1875 | Each | 52500 | 32872
2 | FBE00008 | L.T. 3 Phase 5W cross arms | 26 | 381 | Each | 9906 | 1196
3 | FBE00001 | Back Clamp | 26 | 72 | Each | 1872
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00003 | 55 Sq.mm AAA Conductor | 4.08 | 29490 | K.M. | 120319.2 | 12635.76
6 | CDR00002 | 34 Sq.mm AAA Conductor | 1.02 | 17685 | K.M. | 18038.7 | 1987.98
7 | INS00002 | LT Shackles | 20 | 12 | Each | 240 | 520
8 | HWR00016 | LT metal parts | 20 | 32 | Set | 640
9 | INS00001 | LT Pin Isulator | 96 | 14 | Each | 1344 | 2496
10 | HWR00015 | LT GI Pins | 96 | 29 | Each | 2784 | 52751.74
11 | FBE00048 | MS Strut Clamps for 8.0mts (Set) | 2 | 77 | Each | 154
12 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 16322
13 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 228609.9 | 10886.1857
217723.7143
|  | 3% storage & handling charges on items (1) to (11) |  | 209073.9 |  | 6272.217
|  | 3% Contingencies on Materials |  |  |  | 6858.297
|  | Labour & Transport |  |  |  | 52752
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 6520.1472
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 527.52
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 2175
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 22860.99
[5 empty] | Total | 326576.0712
[5 empty] | or say | 326600
Costdata per Km of LT 3-Ph 5 Wire Line(Horizontal formation ) with
3 x 55 Sq.mm + 2 x 34 Sq.mm AAAC over 8.0Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Rural Areas (MHQs & Major Panchayaths)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00008 | L.T. 3 Phase 5W cross arms | 21 | 381 | Each | 8001 | 966
3 | FBE00001 | Back Clamp | 21 | 72 | Each | 1512
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00003 | 55 Sq.mm AAA Conductor | 3.06 | 29490 | K.M. | 90239.4 | 9476.82
6 | CDR00002 | 34 Sq.mm AAA Conductor | 2.04 | 17685 | K.M. | 36077.4 | 3975.96
7 | INS00002 | LT Shackles | 20 | 12 | Each | 240 | 520
8 | HWR00016 | LT metal parts | 20 | 32 | Set | 640
9 | INS00001 | LT Pin Isulator | 76 | 14 | Each | 1064 | 1976
10 | HWR00015 | LT GI Pins | 76 | 29 | Each | 2204 | 42612.78
11 |  | Concreting of Pole,Stay sets & |  |  | L.S. | 16322
Base concreting
12 |  | Misc. Items like coil earthing, |  |  | L.S. | 3214
pipe earthings, danger-boards, bolts
& nuts, etc.
|  | Total Cost of Material |  |  |  | 200164.8 | 9531.6571
190633.1429
|  | 3% storage & handling charges on items (1) to (10) |  | 180628.8 |  | 5418.864 | 1906.3314
|  | 3% Contingencies on Materials |  |  |  | 6004.944
|  | Labour & Transport |  |  |  | 42613
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5266.9668
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 426.13
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1904
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 20016.48
[5 empty] | Total | 281815.1848
[5 empty] | or say | 281800
Costdata per Km of LT 3-Ph 5 Wire Line(Horizontal formation ) with
5 x 34 Sq.mm AAAC over 8.0 Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00008 | L.T. 3 Phase 5W cross arms | 21 | 381 | Each | 8001 | 966
3 | FBE00001 | Back Clamp | 21 | 72 | Each | 1512
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00002 | 34 Sq.mm AAA Conductor | 5.1 | 17685 | K.M. | 90193.5 | 9939.9
6 | INS00002 | LT Shackles | 20 | 12 | Each | 240 | 520
7 | HWR00016 | LT metal parts | 20 | 32 | Set | 640
8 | INS00001 | LT Pin Isulator | 76 | 14 | Each | 1064
9 | HWR00015 | LT GI Pins | 76 | 29 | Each | 2204 | 1976
10 |  | Concreting of Pole,Stay sets & |  |  |  |  | 39099.9
|  | Base concreting | L.S. |  | L.S. | 16322
11 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts | L.S. |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 164041.5 | 7811.5
156230
|  | 3% storage & handling charges on items (1) to (9) |  | 144505.5 |  | 4335.165
|  | 3% Contingencies on Materials |  |  |  | 4921.245
|  | Labour & Transport |  |  |  | 39100
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4832.76
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 391
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1560
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 16404.15 |  |  |  | 1399.36
[5 empty] | Total | 235585.82
[5 empty] | or say | 235600
Costdata per Km of LT 3-Ph 4 Wire Line(Horizontal formation ) with
4 x 55 Sq.mm AAAC over 8.0 Mts.
PSCC Poles (140Kgs) at 40 Mts. Span in Urban Areas (Corporation & Municipalities)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole (2 poles for strut) | 28 | 1875 | Each | 52500 | 32872
2 | FBE00009 | LT 3-Ph 4W Cross arms with clamp | 26 | 372 | Each | 9672 | 1196
3 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
4 | CDR00003 | 55 Sq.mm AAA Conductor | 4.08 | 29490 | K.M. | 120319.2 | 12635.76
5 | INS00002 | LT Shackles | 16 | 12 | Each | 192 | 416
6 | HWR00016 | LT metal parts | 16 | 32 | Set | 512
7 | INS00001 | LT Pin Isulator | 72 | 14 | Each | 1008 | 1872
8 | HWR00015 | LT GI Pins | 72 | 29 | Each | 2088
9 | FBE00048 | MS Strut Clamps for 8.0mts (Set) | 2 | 77 | Each | 154
10 |  | Concreting of Pole,Stay sets & |  |  |  |  | 50035.76
|  | Base concreting |  |  | L.S. | 16322
11 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 207257.2 | 9869.3905
197387.8095
|  | 3% storage & handling charges on items (1) to (9) |  | 187721.2 |  | 5631.636
|  | 3% Contingencies on Materials |  |  |  | 6217.716
|  | Labour & Transport |  |  |  | 50036
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 6184.4496
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 500.36
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1971
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 20725.72
[5 empty] | Total | 298524.0816
[5 empty] | or say | 298500
Costdata per Km of LT 3 Ph 4 Wire Line(Horizontal formation ) with
4 x 34 Sq.mm AAAC over 8.0 Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00009 | LT 3-Ph 4W Cross arms with clamp | 21 | 372 | Each | 7812 | 966
3 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
4 | CDR00002 | 34 Sq.mm AAA Conductor | 4.08 | 17685 | K.M. | 72154.8 | 7951.92
5 | INS00002 | LT Shackles | 16 | 12 | Each | 192 | 416
6 | HWR00016 | LT metal parts | 16 | 32 | Set | 512
7 | INS00001 | LT Pin Isulator | 57 | 14 | Each | 798 | 1482
8 | HWR00015 | LT GI Pins | 57 | 29 | Each | 1653
9 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 16322 | 36513.92
10 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 143308.8 | 6824.2286
136484.5714
|  | 3% storage & handling charges on items (1) to (8) |  | 123772.8 |  | 3713.184
|  | 3% Contingencies on Materials |  |  |  | 4299.264
|  | Labour & Transport |  |  |  | 36514
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4513.1304
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 365.14
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1363
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 14330.88
[5 empty] | Total | 208407.3984
[5 empty] | or say | 208400
Costdata per Km of LT 3 Ph 4 Wire Line(Horizontal formation ) with
4 x 55 Sq.mm AAAC over 8.0 Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Rural Areas (MHQs & Major Panchayath)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00009 | LT 3-Ph 4W Cross arms with clamp | 21 | 372 | Each | 7812 | 966
3 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
4 | CDR00003 | 55 Sq.mm AAA Conductor | 4.08 | 29490 | K.M. | 120319.2 | 12635.76
5 | INS00002 | LT Shackles | 16 | 12 | Each | 192 | 416
6 | HWR00016 | LT metal parts | 16 | 32 | Set | 512
7 | INS00001 | LT Pin Isulator | 57 | 14 | Each | 798 | 1482
8 | HWR00015 | LT GI Pins | 57 | 29 | Each | 1653
9 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 16322 | 41197.76
10 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 191473.2 | 9117.7714
182355.4286
|  | 3% storage & handling charges on items (1) to (8) |  | 171937.2 |  | 5158.116
|  | 3% Contingencies on Materials |  |  |  | 5744.196
|  | Labour & Transport |  |  |  | 41198
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5092.0728
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 411.98
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1822
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 19147.32
[5 empty] | Total | 270046.8848
[5 empty] | or say | 270000
Costdata per Km of LT S-Ph 3 Wire Line(Horizontal formation )
with 55 Sqmm AAAC over 8.0 Mts.
PSCC Poles (140Kgs) at 40 Mts. Span in Urban Areas (Corporation & Municipalities)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole (2poles for strut) | 28 | 1875 | Each | 52500 | 32872 | 4788
2 | FBE00006 | LT S-Ph 3W Cross arms with clamp | 26 | 391 | Each | 10166 | 1196
3 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044 | 684
4 | CDR00003 | 55 Sq.mm AAA Conductor | 3.06 | 29490 | K.M. | 90239.4 | 9476.82
5 | INS00002 | LT Shackles | 12 | 12 | Each | 144 | 312
6 | HWR00016 | LT metal parts | 12 | 32 | Set | 384
7 | INS00001 | LT Pin Isulator | 48 | 14 | Each | 672 | 1248
8 | HWR00015 | LT GI Pins | 48 | 29 | Each | 1392
9 | FBE00048 | MS Strut Clamps for 8.0mts (Set) | 2 | 77 | Each | 154
10 |  | Concreting of Pole,Stay sets & |  |  |  |  | 46148.82
|  | Base concreting |  |  | L.S. | 16322
11 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 176463.4 | 8403.019
|  | 3% storage & handling charges on items (1) to (9) |  | 156927.4 |  | 4707.822 | 168060.381
|  | 3% Contingencies on Materials |  |  |  | 5293.902
|  | Labour & Transport |  |  |  | 46149
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5704.0164
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 461.49
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1678
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 17646.34
[5 empty] | Total | 258103.9704
[5 empty] | or say | 258100
Costdata per Km of LT S-Ph 3 Wire Line(Horizontal formation )
with 34 Sqmm AAAC over 8.0 Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00006 | LT S-Ph 3W Cross arms with clamp | 21 | 391 | Each | 8211 | 966
3 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
4 | CDR00002 | 34 Sq.mm AAA Conductor | 3.06 | 17685 | K.M. | 54116.1 | 5963.94
5 | INS00002 | LT Shackles | 12 | 12 | Each | 144 | 312
6 | HWR00016 | LT metal parts | 12 | 32 | Set | 384
7 | INS00001 | LT Pin Isulator | 38 | 14 | Each | 532 | 988
8 | HWR00015 | LT GI Pins | 38 | 29 | Each | 1102
9 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 16322 | 33927.94
10 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 124676.1 | 5936.9571
118739.1429
|  | 3% storage & handling charges on items (1) to (8) |  | 105140.1 |  | 3154.203
|  | 3% Contingencies on Materials |  |  |  | 3740.283
|  | Labour & Transport |  |  |  | 33928
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4193.5008
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 339.28
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1186
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 12467.61
[5 empty] | Total | 183684.9768
[5 empty] | or say | 183700
Costdata per Km of LT S-Ph 3 Wire Line(Horizontal formation )
with 55 Sqmm AAAC over 8.0 Mts.
PSCC Poles (140Kgs) at 50 Mts. Span inRural Areas ( MHQs & Major panchayaths)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00006 | LT S-Ph 3W Cross arms with clamp | 21 | 391 | Each | 8211 | 966
3 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
4 | CDR00003 | 55 Sq.mm AAA Conductor | 3.06 | 29490 | K.M. | 90239.4 | 9476.82
5 | INS00002 | LT Shackles | 12 | 12 | Each | 144 | 312
6 | HWR00016 | LT metal parts | 12 | 32 | Set | 384
7 | INS00001 | LT Pin Isulator | 38 | 14 | Each | 532 | 988
8 | HWR00015 | LT GI Pins | 38 | 29 | Each | 1102
9 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 16322 | 37440.82
10 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3214
& nuts, etc.
|  | Total Cost of Material |  |  |  | 160799.4 | 7657.1143
153142.2857
|  | 3% storage & handling charges on items (1) to (8) |  | 141263.4 |  | 4237.902
|  | 3% Contingencies on Materials |  |  |  | 4823.982
|  | Labour & Transport |  |  |  | 37441
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4627.7076
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 374.41
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1530
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 16079.94
[5 empty] | Total | 229914.3416
[5 empty] | or say | 229900
Costdata per Km of LT S-Ph 2 Wire Line(Horizontal formation )
with 2 x 55 Sqmm AAAC over 8.0Mts.
PSCC Poles (140Kgs) at 40 Mts. Span in Urban Areas ( Corporations & Municipalities)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole (2poles for strut) | 28 | 1875 | Each | 52500 | 32872
2 | FBE00033 | L.T. S. Phase 2W cross arms without clamp | 26 | 268 | Each | 6968 | 1196
3 | FBE00001 | Back Clamp | 26 | 72 | Each | 1872
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00003 | 55 Sq.mm AAA Conductor | 2.04 | 29490 | K.M. | 60159.6 | 6317.88
6 | INS00002 | LT Shackles | 8 | 12 | Each | 96 | 208
7 | HWR00016 | LT metal parts | 8 | 32 | Set | 256
8 | INS00001 | LT Pin Isulator | 24 | 14 | Each | 336 | 624
9 | HWR00015 | LT GI Pins | 24 | 29 | Each | 696
10 | FBE00048 | MS Strut Clamps for 8.0mts (Set) | 2 | 77 | Each | 154
11 |  | Concreting of Pole,Stay sets & |  |  |  |  | 42261.88
|  | Base concreting |  |  | L.S. | 11993
12 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3192
& nuts, etc.
|  | Total Cost of Material |  |  |  | 139498.6 | 6642.7905
132855.8095
|  | 3% storage & handling charges on items (1) to (10) |  | 124313.6 |  | 3729.408
|  | 3% Contingencies on Materials |  |  |  | 4184.958
|  | Labour |  |  |  | 42262
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5223.5832
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 422.62
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1328
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 13949.86
[5 empty] | Total | 210599.0292
[5 empty] | or say | 210600
Costdata per Km of LT S-Ph 2 Wire Line(Horizontal formation )
with 2 x 34 Sqmm AAAC over 8.0Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00033 | L.T. S. Phase 2W cross arms without clamp | 21 | 268 | Each | 5628 | 966
3 | FBE00001 | Back Clamp | 21 | 72 | Each | 1512
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00002 | 34 Sq.mm AAA Conductor | 2.04 | 17685 | K.M. | 36077.4 | 3975.96
6 | INS00002 | LT Shackles | 8 | 12 | Each | 96 | 208
7 | HWR00016 | LT metal parts | 8 | 32 | Set | 256
8 | INS00001 | LT Pin Isulator | 24 | 14 | Each | 336 | 624
9 | HWR00015 | LT GI Pins | 24 | 29 | Each | 696
10 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 11993 | 31471.96
11 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3192
& nuts, etc.
|  | Total Cost of Material |  |  |  | 100437.4 | 4782.7333
95654.6667
|  | 3% storage & handling charges on items (1) to (9) |  | 85252.4 |  | 2557.572
|  | 3% Contingencies on Materials |  |  |  | 3013.122
|  | Labour |  |  |  | 31472
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 3889.9392
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 314.72
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 956
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 10043.74
[5 empty] | Total | 152684.4932
[5 empty] | or say | 152700
Costdata per Km of LT S-Ph 2 Wire Line(Horizontal formation )
with 2 x 55 Sqmm AAAC over 8.0Mts.
PSCC Poles (140Kgs) at 50 Mts. Span in Urban Areas (MHQs & Major Panchayath)
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | FBE00033 | L.T. S. Phase 2W cross arms without clamp | 21 | 268 | Each | 5628 | 966
3 | FBE00001 | Back Clamp | 21 | 72 | Each | 1512
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Each | 1276 | 1044
5 | CDR00003 | 55 Sq.mm AAA Conductor | 2.04 | 29490 | K.M. | 60159.6 | 6317.88
6 | INS00002 | LT Shackles | 8 | 12 | Each | 96 | 208
7 | HWR00016 | LT metal parts | 8 | 32 | Set | 256
8 | INS00001 | LT Pin Isulator | 24 | 14 | Each | 336 | 624
9 | HWR00015 | LT GI Pins | 24 | 29 | Each | 696
10 |  | Concreting of Pole,Stay sets &
|  | Base concreting |  |  | L.S. | 11993 | 33813.88
11 |  | Misc. Items like coil earthing,
|  | pipe earthings, danger-boards, bolts |  |  | L.S. | 3192
& nuts, etc.
|  | Total Cost of Material |  |  |  | 124519.6 | 5929.5048
118590.0952
|  | 3% storage & handling charges on items (1) to (9) |  | 109334.6 |  | 3280.038
|  | 3% Contingencies on Materials |  |  |  | 3735.588
|  | Labour & Transport |  |  |  | 33814
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4179.4104
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 338.14
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1185
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 12451.96
[5 empty] | Total | 183503.7364
[5 empty] | or say | 183500
Costdata per Km of LT line with 3 x 16 + 25 Sqmm AB Cable over 8.0 Mts.
PSCC Poles at 65 Mts. Span, 75 Kg/Sq.Mt wind pressure, working load 140 Kgs.
Sl. No. | Material code | Particulars | Qty. Nos | Rate in Rs. | Per Unit | Amount in Rs.
1 | PlS00001 | 8.0mts PSCC Pole | 16 | 1875 | Each | 30000 | 18784
2 | HWR00012 | Hardware Suspension clamp (eye hook) | 14 | 175 | Each | 2450 | 364
3 | HWR00009 | Dead end clamp with eye hook | 4 | 113 | Each | 452 | 104
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Set | 1276 | 1044
5 | CBA00003 | L.T. A.B. Cable 3 x 16 + 25 Sqmm | 1.02 | 49000 | K.M. | 49980 | 5461.08
6 | SCB00058 | LT Connector for AB Cable with insulation | 64 | 82 | Each | 5248 | 1664
7 |  | Concreting of Pole,Stay concreting & |  |  |  |  | 27421.08
|  | Base concreting |  |  | L.S. | 16322
8 |  | Misc. Items like coil earthing,
|  | bolts & nuts, etc. |  |  | L.S. | 3214
|  | Total Cost of Material |  |  |  | 108942 | 5187.7143
103754.2857
|  | 3% storage & handling charges on items (1) to (6) |  | 89406 |  | 2682.18
|  | 3% Contingencies on Materials |  |  |  | 3268.26
|  | Labour & Transport |  |  |  | 27421
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 3389.2356
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 274.21
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1037
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 10894.2
[5 empty] | Total | 157908.0856
[5 empty] | or say | 157900
Costdata per Km of LT line with 2 x 16 + 25 Sqmm AB Cable over 8.0Mts.
PSCC Poles(140 kgs) at 50 Mts. Span in Rural areas.
Sl. No. | Material code | Particulars | Qty.Nos | Rate in Rs. | Per Unit | Amount in Rs.
1 | PlS00001 | 8.0mts PSCC Pole | 21 | 1875 | Each | 39375 | 24654
2 | HWR00012 | Hardware Suspension clamp (eye hook) | 19 | 175 | Each | 3325 | 494
3 | HWR00009 | Dead end clamp with eye hook | 4 | 113 | Each | 452 | 104
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Set | 1276 | 1044
5 | CBA00002 | L.T. A.B. Cable 2 x 16 + 25 Sqmm | 1.02 | 34350 | K.M. | 35037 | 4002.48
6 | SCB00058 | LT Connector for AB Cable with insulation | 63 | 82 | Each | 5166 | 1638
7 |  | Concreting of Pole,Stay concreting & |  |  |  |  | 31936.48
|  | Base concreting |  |  | L.S. | 16322
8 |  | Misc. Items like coil earthing,
|  | bolts & nuts, etc. |  |  | L.S. | 3214
|  | Total Cost of Material |  |  |  | 104167 | 4960.3333
99206.6667
|  | 3% storage & handling charges on items (1) to (6) |  | 84631 |  | 2538.93
|  | 3% Contingencies on Materials |  |  |  | 3125.01
|  | Labour & Transport |  |  |  | 31936
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 3947.2896
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 319.36
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 979
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 10416.7
[5 empty] | Total | 157429.2896
[5 empty] | or say | 157400
R.E.C. - Construction Standard No. B-32/1984
Costdata per Km of LT line with 3 x 16 + 25 Sqmm AB Cable over 8.0 Mts.
PSCC Poles at 65 Mts. Span, 100 Kg/Sq.Mt wind pressure, working load 200 Kgs.
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00002 | 8.0mts PSCC Pole | 16 | 1995 | Each | 31920 | 18784
2 | HWR00012 | Hardware Suspension clamp (eye hook) | 14 | 175 | Each | 2450 | 364
3 | HWR00009 | Dead end clamp with eye hook | 4 | 113 | Each | 452 | 104
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Set | 1276 | 1044
5 | CBA00003 | L.T. A.B. Cable 3 x 16 + 25 Sqmm | 1.02 | 49000 | K.M. | 49980 | 5461.08
6 | SCB00058 | LT Connector for AB Cable with insulation | 64 | 82 | Each | 5248 | 1664
7 |  | Concreting of Pole,Stay concreting & |  |  |  |  | 27421.08
|  | Base concreting |  |  | L.S. | 16322
8 |  | Misc. Items like coil earthing,
|  | bolts & nuts, etc. |  |  | L.S. | 3214
|  | Total Cost of Material |  |  |  | 110862 | 5279.1429
105582.8571
|  | 3% storage & handling charges on items (1) to (6) |  | 91326 |  | 2739.78
|  | 3% Contingencies on Materials |  |  |  | 3325.86
|  | Labour & Transport |  |  |  | 27421
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 3389.2356
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 274.21
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1053
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 11086.2
[5 empty] | Total | 160151.2856
[5 empty] | or say | 160200
R.E.C. - Construction Standard No. B-32/1984
Costdata per Km of LT line with 2 x 16 + 25 Sqmm AB Cable over 8.0 Mts.
PSCC Poles (200Kgs) at 50 Mts. Span in Rural Areas
Sl. No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | PLS00002 | 8.0mts PSCC Pole | 21 | 1995 | Each | 41895 | 24654
2 | HWR00012 | Hardware Suspension clamp (eye hook) | 19 | 175 | Each | 3325 | 494
3 | HWR00009 | Dead end clamp with eye hook | 4 | 113 | Each | 452 | 104
4 | FBE00028 | MS Stay sets with clamps | 4 | 319 | Set | 1276 | 1044
5 | CBA00002 | L.T. A.B. Cable 2 x 16 + 25 Sqmm | 1.02 | 34350 | K.M. | 35037 | 4002.48
6 | SCB00058 | LT Connector for AB Cable with insulation | 63 | 82 | Each | 5166 | 1638
7 |  | Concreting of Pole,Stay concreting & |  |  |  |  | 31936.48
|  | Base concreting |  |  | L.S. | 16322
8 |  | Misc. Items like coil earthing,
|  | bolts & nuts, etc. |  |  | L.S. | 3214
|  | Total Cost of Material |  |  |  | 106687 | 5080.3333
101606.6667
|  | 3% storage & handling charges on items (1) to (6) |  | 87151 |  | 2614.53
|  | 3% Contingencies on Materials |  |  |  | 3200.61
|  | Labour & Transport |  |  |  | 31936
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 3947.2896
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 319.36
|  | BW Welfare cess @ 1% on cost of material (Excluding VAT) |  |  |  | 1000
|  | 10% Estt. & Genl. Charges on Materials |  |  |  | 10668.7
[5 empty] | Total | 160373.4896
[5 empty] | or say | 160400
Note on C216: APSPDCL: with clamps
Note on C257: APSPDCL: with clamps
Note on C297: APSPDCL: with clamps

## Errection-Tran.(P.45-48)
R.E.C. - Construction Standard Specification No. F3&F4/1981
Cost Data For Erection Of 100KVA-11KV/433V CSP Transformer
(Without LV Side Metering)
Sl. No. | Material code | Particulars | Cost of Material (Rs.) | Labour & Transport (Rs.)
1 | DTC30006 | 11 KV/433V 100KVA CSP TRANSFORMER | 144150 | 1354
2 | ABS10002 | 11 KV 200Amps TT AB Switch with insulators | 8322 | 1279
3 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 2493 | 271
4 | HGF00004 | L.T.3-Ph H.G. Fuse sets (2 Nos.) | 3460 | 404
5 | LAS00001 | 11KV Lightning Arrestors | 4419 | 422
6 |  | S.P structure (Including Earthing) | 25546 | 10562 | 11618.2
7 |  | Solid Plinth/Pillar mounted plinth for DTR |  | 11000
8 |  | Misc. Items | 480
|  | Total Cost of Material | 188870 | 25292 | 8993.8095
179876.1905
|  | 3% storage & handling charges | 5666.1
|  | 3% Contingencies on Materials | 5666.1
|  | Labour & Transport | 25292
|  | Service Tax @ 12.36% on Labour & Transport | 3126.0912
|  | BW Welfare cess @ 1% on Labour & Transport | 252.92
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | 1786 |  |  | 1000
|  | 10% Estt. & Genl. Charges on Materials | 18887
|  | Total Cost in Rs. | 249546.2112
|  | or say : | 249500
R.E.C. - Construction Standard Specification No. F3&F4/1981
Cost Data For Erection Of 100KVA-11KV/433V
….
(Without LV Side Metering)
Sl. No. | Material code | Particulars | Cost of Material (Rs.) | Labour & Transport (Rs.)
1 | DTA30006 | 11 KV/433V 100KVA Amorphous Distribution Transformer | 144150 | 1354 | 1585.3986
2 | ABS10002 | 11 KV 200Amps TT AB Switch with insulators | 8322 | 1279 | 1497.5811
3 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 2493 | 271 | 317.3139
4 | HGF00004 | L.T.3-Ph H.G. Fuse sets (2 Nos.) | 3460 | 404 | 473.0436
5 | LAS00001 | 11KV Lightning Arrestors | 4419 | 422
6 |  | S.P structure (Including Earthing) | 25546 | 10562 | 11618.2
7 |  | Solid Plinth/Pillar mounted plinth for DTR |  | 11000
8 |  | Misc. Items | 480
|  | Total Cost of Material | 188870 | 25292 | 8993.8095
179876.1905
|  | 3% storage & handling charges | 5666.1
|  | 3% Contingencies on Materials | 5666.1
|  | Labour & Transport | 25292
|  | Service Tax @ 12.36% on Labour & Transport | 3126.0912
|  | BW Welfare cess @ 1% on Labour & Transport | 252.92
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | 1786
|  | 10% Estt. & Genl. Charges on Materials | 18887
|  | Total Cost in Rs. | 249546.2112
|  | or say : | 249500
R.E.C. - Construction Standard Specification No. F3&F4/1981
Cost Data For Erection Of 63KVA-11KV/433V CSP Transformer
(Without LV Side Metering)
Sl. No. | Material code | Particulars | Cost of Material (Rs.) | Labour & Transport (Rs.)
1 | DTC30004 | 11 KV/433V 63KVA CSP Distribution Transformer | 115200 | 1354 | 1585.3986
2 | ABS10002 | 11 KV 200Amps TT AB Switch with insulators | 8322 | 1279 | 1497.5811
3 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 2493 | 271 | 317.3139
4 | HGF00004 | L.T.3-Ph H.G. Fuse sets | 3460 | 404 | 473.0436
5 | LAS00001 | 11KV Lightning Arrestors | 4419 | 422
6 |  | S.P structure (Including Earthing) | 25546 | 10562 | 11618.2
7 |  | Solid Plinth/Pillar mounted plinth for DTR |  | 11000
8 |  | Misc. Items | 480
|  | Total Cost of Material | 159920 | 25292 | 7615.2381
152304.7619
|  | 3% storage & handling charges on items 1 to 5 | 4797.6
|  | 3% Contingencies on Materials | 4797.6
|  | Labour & Transport | 25292 |  | 29614.4028
0
|  | Service Tax @ 12.36% on Labour & Transport | 3126.0912
|  | BW Welfare cess @ 1% on Labour & Transport | 252.92
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | 1523
|  | 10% Estt. & Genl. Charges on Materials | 15992
|  | Total Cost in Rs. | 215701.2112
|  | or say : | 215700
R.E.C. - Construction Standard Specification No. F3&F4/1981
Cost Data For Erection Of 63KVA-11KV/433V CSP Amorphous Metal Core Transformer
(Without LV Side Metering)
Sl. No. | Material code | Particulars | Cost of Material (Rs.) | Labour & Transport (Rs.)
1 | DTA30004 | 11 KV/433V 63KVA Amorphous Distribution Transformer | 115200 | 1354 | 1585.3986
2 | ABS10002 | 11 KV 200Amps TT AB Switch with insulators | 8322 | 1279 | 1497.5811
3 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 2493 | 271 | 317.3139
4 | HGF00004 | L.T.3-Ph H.G. Fuse sets | 3460 | 404 | 473.0436
5 | LAS00001 | 11KV Lightning Arrestors | 4419 | 422
6 |  | S.P structure (Including Earthing) | 25546 | 10562 | 11618.2
7 |  | Solid Plinth/Pillar mounted plinth for DTR |  | 11000
8 |  | Misc. Items | 480
|  | Total Cost of Material | 159920 | 25292 | 7615.2381
152304.7619
|  | 3% storage & handling charges on items 1 to 6 | 4797.6
8728.5
|  | 3% Contingencies on Materials | 4797.6
|  | Labour & Transport | 25292 |  | 27821.2
|  | Service Tax @ 12.36% on Labour & Transport | 3126.0912
|  | BW Welfare cess @ 1% on Labour & Transport | 252.92
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | 1523
|  | 10% Estt. & Genl. Charges on Materials | 15992
|  | Total Cost in Rs. | 215701.2112
|  | or say : | 215700

## 25KVA Pole 140-49
Erection of 25KVA-11KV/433V Coper Wound Distribution Transformer for Releasing of Agrl Services
Sl. No. | Material code | Particulars | Qty | Cost of Material (Rs.) | Labour & Transport (Rs.) | Total
1 | PLS00002 | 8.0 mts 140Kgs PSCC pole | 1 | 1875 | 1174 | 3049
2 | DTC30102 | 3-Ph 25KVA DTR CRGO conventional | 1 | 61216 | 1083 | 62299
3 | FBG00018 | Mounting arrangements for DTrs | 1 | 2019 | 271 | 2290
4 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 1 | 2493 | 271 | 2764
5 | FBE00027 | LT open wiring fuse sets structure | 1 | 752 | 1518 | 2270
6 | HGF00004 | L.T.3-Ph H.G. Fuse sets | 1 | 1730 | 202 | 1932
7 | EMT00006 | Earthing of DTR with 80mm dia 6mm thick 2.54mts CI earth pipe | 2 | 4942 | 2070 | 7012
1372
8 | FBE10022 | MS Stay sets with clamps | 2 | 896 | 522 | 1418
9 | MTE30001 | Metering arrangement | 1 | 1890 | 1390 | 3280
452
10 |  | Miscellanious | LS | 1050 |  | 1050
|  | Total Cost of Material |  | 78863 | 8501 | 87364 | 3755.381
75107.619
|  | 3% storage & handling charges |  | 2365.89
|  | 3% Contingencies on Materials |  | 2365.89
|  | Labour & Transport |  | 8501 |  |  | 9953.8209
|  | Service Tax @ 12.36% on Labour & Transport |  | 1050.7236
|  | BW Welfare cess @ 1% on Labour & Transport |  | 85.01
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  | 751
|  | 10% Estt. & Genl. Charges on Materials |  | 7886.3
|  | Total Cost in Rs. |  | 101868.8136
|  | or say : |  | 101900

## 25KVA Pole 200-50
Erection of 25KVA-11KV/433V Coper Wound Distribution Transformer for Releasing of Agrl Services
Sl. No. | Material code | Particulars | Qty | Cost of Material (Rs.) | Labour & Transport (Rs.) | Total
1 | PLS00002 | 8.0 mts 200Kgs PSCC pole | 1 | 1995 | 1174 | 3169 | 1374.6366
2 | DTC30102 | 3-Ph 25KVA DTR CRGO conventional | 1 | 61216 | 1083 | 62299 | 1268.0847
3 | FBG00018 | Mounting arrangements for DTrs | 1 | 2019 | 271 | 2290 | 317.3139
4 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 1 | 2493 | 271 | 2764 | 317.3139
5 | FBE00027 | LT open wiring fuse sets structure | 1 | 752 | 1518 | 2270 | 1777.4262
6 | HGF00004 | L.T.3-Ph H.G. Fuse sets | 1 | 1730 | 202 | 1932 | 236.5218
7 | EMT00006 | Earthing of DTR with 80mm dia 6mm thick 2.54mts CI earth pipe | 2 | 4942 | 2070 | 7012 | 2423.763
8 | FBE10022 | MS Stay sets with clamps | 2 | 896 | 522 | 1418 | 611.2098
9 | MTE30001 | Metering arrangement | 1 | 1890 | 1390 | 3280 | 1627.551
10 |  | Miscellanious | LS | 1050 |  | 1050
|  | Total Cost of Material |  | 78983 | 8501 | 87484 | 3761.0952
75221.9048
|  | 3% storage & handling charges |  | 2369.49
|  | 3% Contingencies on Materials |  | 2369.49
|  | Labour & Transport |  | 8501 |  |  | 9953.8209
|  | Service Tax @ 12.36% on Labour & Transport |  | 1050.7236
|  | BW Welfare cess @ 1% on Labour & Transport |  | 85.01
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  | 752
|  | 10% Estt. & Genl. Charges on Materials |  | 7898.3
|  | Total Cost in Rs. |  | 102009.0136
|  | or say : |  | 102000

## 16KVA Pole.140-51
Erection of 16KVA-11KV/433V Coper Wound Distribution Transformer for Releasing of Agrl Services
Sl. No. | Material code | Particulars | Qty | Cost of Material (Rs.) | Labour & Transport (Rs.) | Total
1 | PLS00002 | 8.0 mts 140Kgs PSCC pole | 1 | 1875 | 1174 | 3049 | 1374.6366
2 | DTC30132 | 3-Ph 16KVA DTR CRGO/AMARPHOUS 5* RATING (COPPER) | 1 | 69668 | 1083 | 70751 | 1268.0847
3 | FBG00018 | Mounting arrangements for DTrs | 1 | 2019 | 271 | 2290 | 317.3139
4 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 1 | 2493 | 271 | 2764 | 317.3139
5 | FBE00027 | LT open wiring fuse sets structure | 1 | 752 | 1518 | 2270 | 1777.4262
6 | HGF00004 | L.T.3-Ph H.G. Fuse sets | 1 | 1730 | 202 | 1932 | 236.5218
7 | EMT00006 | Earthing of DTR with 80mm dia 6mm thick 2.54mts CI earth pipe | 2 | 4942 | 2070 | 7012 | 2423.763
8 | FBE10022 | MS Stay sets with clamps | 2 | 896 | 522 | 1418 | 611.2098
9 | MTE30001 | Metering arrangement | 1 | 1890 | 1390 | 3280 | 1627.551
10 |  | Miscellanious | LS | 1050 |  | 1050
|  | Total Cost of Material |  | 87315 | 8501 | 95816 | 4157.8571
83157.1429
|  | 3% storage & handling charges |  | 2619.45
|  | 3% Contingencies on Materials |  | 2619.45
|  | Labour & Transport |  | 8501
|  | Service Tax @ 12.36% on Labour & Transport |  | 1050.7236
|  | BW Welfare cess @ 1% on Labour & Transport |  | 85.01
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  | 832
|  | 10% Estt. & Genl. Charges on Materials |  | 8731.5
|  | Total Cost in Rs. |  | 111754.1336
|  | or say : |  | 111800

## 16KVA Pole.200-52
Erection of 16KVA-11KV/433V Coper Wound Distribution Transformer for Releasing of Agrl Services
Sl. No. | Material code | Particulars | Qty | Cost of Material (Rs.) | Labour & Transport (Rs.) | Total
1 | PLS00002 | 8.0 mts 200Kgs PSCC pole | 1 | 1995 | 1174 | 3169 | 1374.6366
2 | DTC30132 | 3-Ph 16KVA DTR CRGO/AMARPHOUS 5* RATING (COPPER) | 1 | 69668 | 1083 | 70751 | 1268.0847
3 | FBG00018 | Mounting arrangements for DTrs | 1 | 2019 | 271 | 2290 | 317.3139
4 | HGF10002 | 11 KV 3-Ph H.G. Fuse set | 1 | 2493 | 271 | 2764 | 317.3139
5 | FBE00027 | LT open wiring fuse sets structure | 1 | 752 | 1518 | 2270 | 1777.4262
6 | HGF00004 | L.T.3-Ph H.G. Fuse sets | 1 | 1730 | 202 | 1932 | 236.5218
7 | EMT00006 | Earthing of DTR with 80mm dia 6mm thick 2.54mts CI earth pipe | 2 | 4942 | 2070 | 7012 | 2423.763
8 | FBE10022 | MS Stay sets with clamps | 2 | 896 | 522 | 1418 | 611.2098
9 | MTE30001 | Metering arrangement | 1 | 1890 | 1390 | 3280 | 1627.551
10 |  | Miscellanious | LS | 1050 |  | 1050
|  | Total Cost of Material |  | 87435 | 8501 | 95936 | 4163.5714
83271.4286
|  | 3% storage & handling charges |  | 2623.05
|  | 3% Contingencies on Materials |  | 2623.05
|  | Labour & Transport |  | 8501
|  | Service Tax @ 12.36% on Labour & Transport |  | 1050.7236
|  | BW Welfare cess @ 1% on Labour & Transport |  | 85.01
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  | 833
|  | 10% Estt. & Genl. Charges on Materials |  | 8743.5
|  | Total Cost in Rs. |  | 111894.3336
|  | or say : |  | 111900

## Errection S-PH(P.53-54)
R.E.C. - Construction Standard Specification No. F3&F4/1981
Cost Data for Erection of 15KVA Single Phase 6.3KV/0-240V
CSP Transformer (Oil Immersed) On existing 8.0mts PSCC Support
Sl.No | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | DTC10004 | S-Ph 15KVA DTR CRGO CSP | 1 No. | 37522 | Each | 37522
2 | FBE00044 | Mounting arrangements for Transformer | 1 Set | 356 | Each | 356
3 |  | Pipe earthing | 2 No. | 1300 | Each | 2600
4 |  | Misc. Items | L.S. | L.S. | L.S. | 435
|  | Total Cost of Material |  |  |  | 40913 | 1948.2381
38964.7619
|  | 3% storage & handling charges |  |  |  | 1214.34
|  | 3% Contingencies on Materials |  |  |  | 1214.34
|  | Labour & Transport |  |  |  | 3308 | 3638.8
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 408.8688
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 33.08
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 390
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 4091.3
|  | Total Cost in Rs. |  |  |  | 51572.9288
|  | Or say : |  |  |  | 51600
R.E.C. - Construction Standard Specification No. F3&F4/1981
Cost Data for Erection of 15KVA Single Phase 6.3KV/0-240V
Amorphous Metal Core C.S.P. Transformer (Oil Immersed)
On existing 8.0mts PSCC Supports
Sl.No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | DTA10003 | S-Ph 15KVA DTR amorphous | 1 No. | 37522 | Each | 37522 | 694
2 | FBE00044 | Mounting arrangements for Transformer | 1 Set | 356 | Each | 356 | 231
3 |  | Pipe earthing | 2 No. | 1300 | Each | 2600 | 1042
4 |  | Misc. Items | L.S. | L.S. | L.S. | 435
|  | Total Cost of Material |  |  |  | 40913 | 1948.2381
38964.7619
|  | 3% storage & handling charges |  |  |  | 1214.34
|  | 3% Contingencies on Materials |  |  |  | 1214.34
|  | Labour & Transport |  |  |  | 3308 | 3638.8
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 408.8688
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 33.08
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 390
|  | 10% Estt. & Genl. Charges On Materials |  |  |  | 4091.3
|  | Total Cost in Rs. |  |  |  | 51572.9288
|  | Or say : |  |  |  | 51600

## P(55-56)
R.E.C. - Construction Standard Specification No. H6&H8/1981 | [7 empty] | H6&H8/1981
Cost Data for Single Phase Water Works Service erected on Supports
Sl.No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | MTE10018 | 1 Phase (5-30A) High Quality Energy meter | 1 | 948 | Each | 948
2 | BXS00147 | Moulded Distribution Box | 1 | 433 | Each | 433
3 |  | 1 Phase 15A M.C.B./Fuse Unit | 1 | 150 | Each | 150
4 |  | P.V.C. Cable 6 Sq.mm Single Core | 20 | 44 | Mts | 880
5 |  | P.V.C. Bends 38mm | 1 | 20 | Each | 20
6 |  | Bolts, Nuts etc. | L.S. | L.S. | L.S. | 100
|  | Total Cost of Material |  |  |  | 2531 | 120.5238
2410.4762
|  | 3% Contingencies |  |  |  | 75.93
|  | Labour & Transport |  |  |  | 1076 | 1183.6
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 132.9936
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 10.76
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 24
|  | 10% Estt. & Genl. Charges |  |  |  | 253.1
|  | Total Cost in Rs. |  |  |  | 4103.7836
|  | Or say : |  |  |  | 4100
R.E.C. - Construction Standard Specification No. H6&H8/1981
Cost Data for Release of Poly Phase Agriculture Service Erected on Supports
Sl.No. | Material code | Particulars | Qty. | Rate in Rs. | Per Unit | Amount in Rs.
1 | MTE30001 | 3-Phase (10- 40 A ) Electronic Meter with PP Box | 1 | 1890 | Each | 1890
2 | BXS00147 | Moulded Distribution Box | 1 | 433 | Each | 433
3 |  | 3 Phase 40A M.C.B./Fuse Unit (3 Nos.) | 1 | 580 | Each | 580
4 |  | P.V.C. Cable 4 Sq.mm Single Core | 40 | 35 | Mts | 1400
5 |  | Misc. items such as Bolts, Nuts & Board etc. | L.S. | L.S. | L.S. | 100
|  | Total Cost of Material |  |  |  | 4403 | 209.6667
4193.3333
|  | 3% Contingencies |  |  |  | 132.09
|  | Labour & Transport |  |  |  | 1681 | 1849.1
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 207.7716
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 16.81
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 42
|  | 10% Estt. & Genl. Charges |  |  |  | 440.3
|  | Total Cost in Rs. |  |  |  | 6922.9716
|  | Or say : |  |  |  | 6900

## P(57-60)
R.E.C. - Construction Standard Specification No. H1 TO H3/1981
Cost Data for Domestic and Non-Domestic Service Connection
(Single Phase) With Electronic Meter High Quality Meter
Sl. No. | Material code | Particulars | Rate | Chargable to DISCOM |  | Chargable to Consumer |  | Amount in Rs.
|  |  |  | Qty . | Amount | Qty. | Amount
1 | MTE10018 | LT Single Phase 5-30A Electronic Energy meter | 948 | 1 | 948 |  |  | 948
2 | BXS00147 | Moulded Distribution Box | 433 | 1 | 433 |  |  | 433
3 | WRS00005 | G.I. Wire No.8 | 64/kg |  |  | 1 Kg. | 64 | 64
4 |  | 15A M.C.B./Fuse Unit | 150/E | 1 | 160 |  |  | 160
5 |  | P.V.C. Cable single core 2.5 Sq.mm | 22/M |  |  | 60 | 1320 | 1320
6 |  | P.V.C. Pipe 20mm | 25/M |  |  | 2 M | 50 | 50
7 |  | P.V.C. Bends 20mm | 5/E |  |  | 2 Nos. | 10 | 10
8 |  | Misc. | L.S |  |  |  | 70 | 70
|  | Total |  |  | 1541 |  | 1514 | 3055 | 145.4762
2909.5238
|  | 3% Contingencies on Materials |  |  | 46.23 |  | 45.42 | 91.65
|  | Labour & Transport |  |  | 290 |  | 610 | 900
|  | Service Tax @ 12.36% on Labour & Transport | [5 empty] | 111.24
|  | BW Welfare cess @ 1% on Labour & Transport | [5 empty] | 9
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | [5 empty] | 29
|  | 10% Estt. & Genl. Charges |  |  | 154.1 |  | 151.4 | 305.5
|  | Total Cost in Rs. |  |  | 2031.33 |  | 2320.82 | 4501.39
|  | Or say : | [5 empty] | 4500
Note : |  | Item Nos. 4 to 7 are to be borne & arranged by the Consumer.
R.E.C. - Construction Standard Specification No. H1 TO H3/1981
Cost Data for Domestic and Non-Domestic Service Connection
(Three Phase) With Electronic Meter High Quality Meter
Sl. No. | Material code | Particulars | Rate | Chargable to DISCOM |  | Chargable to Consumer |  | Amount in Rs.
|  |  |  | Qty . | Amount | Qty. | Amount
1 | MTE30001 | LT Three Phase Electronic Meter (with PP Meter Box) 10A - 40A | 1890 | 1 | 1890 |  |  | 1890
2 | BXS00147 | Moulded Distribution Box | 433 | 1 | 433 |  |  | 433
3 | WRS00005 | G.I. Wire No.8 | 64/KG |  |  | 1 Kg. | 64 | 64
4 |  | 3 phase 60A M.C.B./Fuse unit | 590/E | 1 | 590 |  |  | 590
5 |  | P.V.C. Cable single core 2.5 Sq.mm | 22/M |  |  | 120 Mts. | 2640 | 2640
6 |  | P.V.C. Pipe 20mm | 25/M |  |  | 2 M | 50 | 50
7 |  | P.V.C. Bends 20mm | 5/E |  |  | 2 Nos. | 10 | 10
8 |  | Misc. | L.S |  |  |  | 80 | 80
|  | Total |  |  | 2913 |  | 2844 | 5757 | 274.1429
5482.8571
|  | 3% Contingencies on Materials |  |  | 87.39 |  | 85.32 | 172.71
|  | Labour & Transport |  |  | 575 |  | 790 | 1365 | 652.05
|  | Service Tax @ 12.36% on Labour & Transport | [5 empty] | 168.714
|  | BW Welfare cess @ 1% on Labour & Transport | [5 empty] | 13.65
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | [5 empty] | 55
|  | 10% Estt. & Genl. Charges |  |  | 291.3 |  | 284.4 | 575.7
|  | Total Cost in Rs. |  |  | 3866.69 |  | 4003.72 | 8107.774
|  | Or say : | [5 empty] | 8100
Note : |  | Item Nos. 4 to 7 are to be borne & arranged by the Consumer.
R.E.C. - Construction Standard Specification No. H-5/1981
Cost Data for Poly Phase Service Connection Charges for
Erection of 1No Industrial Service (Upto 15 H.P.) (High Quality Meter)
Sl. No. | Material code | Particulars | Rate | Chargable to DISCOM |  | Chargable to Consumer |  | Amount in Rs.
|  |  |  | Qty . | Amount | Qty. | Amount
1 | MTE30001 | LT Three Phase Electronic Meter (with PP Meter Box) 10A - 40A | 1890 | 1 | 1890 |  |  | 1890
2 | WRS00005 | G.I. Wire No.8 | 64/Kg |  |  | 1 Kg. | 64 | 64
3 |  | 3 phase 60A M.C.B./Fuse unit | 590/E | 1 | 590 |  |  | 590
4 |  | P.V.C. Cable single core 6Sq.mm | 44/M |  |  | 80 | 3520 | 3520 | 3520
5 |  | P.V.C. Pipe 38mm | 105/M |  |  | 2 M |  | 210
6 |  | P.V.C. Bends 38mm | 22/E |  |  | 2 Nos. | 44 | 44
7 |  | Misc. items viz. link clips, wooden box, Bolts & Nuts. | L.S |  | 70 |  | 120 | 190
|  | Total |  |  | 2550 |  | 3748 | 6508 | 309.9048
6198.0952
|  | 3% Contingencies |  |  | 76.5 |  | 112.44 | 188.94
|  | Labour & Transport |  |  | 575 |  | 790 | 1365 | 632.5
|  | Service Tax @ 12.36% on Labour & Transport | [5 empty] | 168.714
|  | BW Welfare cess @ 1% on Labour & Transport | [5 empty] | 13.65
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | [5 empty] | 62
|  | 10% Estt. & Genl. Charges |  |  | 255 |  | 374.8 | 629.8
|  | Total Cost in Rs. |  |  | 3456.5 |  | 5025.24 | 8936.104
|  | Or say : | [5 empty] | 8900
R.E.C. - Construction Standard Specification No. H-5/1981
Cost Data for Poly Phase Service Connection Charges for
Erection of 1No Industrial Service (Above 15 H.P.) (C.T. Meter)
Sl. No. | Material code | Particulars | Rate | Chargable to DISCOM |  | Chargable to Consumer |  | Amount in Rs.
|  |  |  | Qty. | Amount | Qty. | Amount
1 | MCT30004 | L.T. 3-Phase class-0.5 Accuracy CT Operated Energy Meter Housed in a box | 7210 | 1 | 7210 |  |  | 7210
2 | WRS00005 | G.I. Wire No.8 | 64/Kg |  |  | 1 Kg. | 64 | 64
3 |  | P.V.C. Cable single core 6 Sq.mm | 44/M |  |  | 3 | 132 | 132 | 132
4 |  | P.V.C. Pipe 38mm | 105/M |  |  | 2 M | 210 | 210
5 |  | P.V.C. Bends 38mm | 22/E |  |  | 2 Nos. | 44 | 44
6 |  | Misc. items viz. link clips, wooden box, Bolts & Nuts. | L.S |  | 70 |  | 90 | 160
|  | Total |  |  | 7280 |  | 540 | 7820 | 372.381
7447.619
|  | 3% Contingencies |  |  | 218.4 |  | 16.2 | 234.6
|  | Labour & Transport |  |  | 575 |  | 790 | 1365
|  | Service Tax @ 12.36% on Labour & Transport | [5 empty] | 168.714
|  | BW Welfare cess @ 1% on Labour & Transport | [5 empty] | 13.65
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) | [5 empty] | 74
|  | 10% Estt. & Genl. Charges |  |  | 728 |  | 54 | 782
|  | Total Cost in Rs. |  |  | 8801.4 |  | 1400.2 | 10457.964
|  | Or say : | [5 empty] | 10500

## P 61
Cost Data for erection of 1No LT Electronic Trivector Meters on LV Side of DTR
Sl. No. | Material code | Particulars | Qty | Unit | Rate per (in Rs.) | Amount (in Rs.)
1 | MCT30039 | LT 3--ph 4 wire 200/5A CT Operated TVR meter CL 0.5 S | 1 | Each | 6922 | 6922
2 |  | Mounting Arrangements (M.S. Angle 50x50x6 MM & M.S. Flat 50x6 MM support to meter box with suitable clamps, bolts and nuts) | 1 | per Location | 480 | 480
3 |  | Cleat wiring alternation support M.S. Angle 50x50x6 MM to the 3.5 Core 185 or 120 XLPE LT Cable to LT side of DTR with suitable bolts and nuts including loading, unloading and transport of material to the work site where ever necessary with Lugs 3 x 185 Sq.mm 6 Nos. and 1 x 150 Sq.mm 2 Nos. | 1 | per Location | 1800 | 1800
4 |  | Misc.items viz.lugs (3 x 185 Sq.mm 6 Nos. and 1 x 150 Sq.mm 2 Nos). boits and nuts etc. | LS | LS | 230 | 230
Total | [5 empty] | 9432 | 449.1429
8982.8571
|  | 3% Contingencies |  |  |  | 276.06
|  | Labour & Transport |  |  |  | 2010 | 1669.8
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 248.436
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 20.1
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 90
|  | 10% Estt. & Genl. Charges |  |  |  | 943.2
|  | Total Cost in Rs. |  |  |  | 13019.796
|  | Or say : |  |  |  | 13000

## p 62
Estimate for erection of Metering of LT Industrial Service Load upto 50 to 100HP on 11KV side
S.No. | Material code | Particulars | Qty. | Rate | Per | Material | Labour
1 |  | DP Structure
| PLS00002 | a) 8.0 mts PSCC poles | 3 | 1995 | Each | 5985 | - | 2613
| MST00013 | b) MS Channel 75 x 40 mm | 200 | 53.9 | Kg | 10780 | -
| MST00015 | c) MS Flat 75x 8 / 50 x 6 mm | 50 | 53.9 | Kg | 2695 | -
| MST00003 | d) MS Angle 65 x 65x6 mm | 40 | 53.9 | Kg | 2156 | -
|  | e) Mounting arrangements for plinth | 1 | 3300 | Each | 3300 | -
|  | Labour & Transport | - | - | - | - | 10562 | 11618.2
2 |  | Isolating Switches
| ABS10002 | a) 11 KV AB Switch ( 200 A) | 1 | 8322 | Each | 8322 | -
| HGF10002 | b) 11 KV HG Fuse set | 2 | 2493 | Each | 4986 | -
|  | Labour & Transport | - | - | - | - | 1328 | 1460.8
3 |  | 11 KV Metering Equipment
| MHT10005 | a) 11 KV Trivector Meter | 1 | 4305 | Each | 4305 | -
| ITR10083 | b) 11 KV Metering Set ( 5/5 A) | 1 | 32497 | Each | 32497 | -
|  | Labour & Transport | - | - | - | - | 5287 | 5815.7
4 |  | 11 KV Cable
| CBX10002 | a) 11 KV UG Cable 3x35 sqmm | 20 | 340 | mts | 6800 | -
| SCB00025 | b) 11 KV Out door joining links | 2 | 773 |  | 1546 | -
|  | Labour & Transport | - | - | - | - | 4287 | 4715.7
5 |  | 11 KV LAS
| LAS00001 | a) 11 KV metal oxide 10 KA Las | 3 | 1473 | Each | 4419 | 500 | 550
6 |  | Earthing complete with Earth pipes | 4 | 1300 | Each | 5200 | 2521 | 2773.1
7 | BXS00011 | A Type Distribution box | 1 | 6960 | Each | 6960 | 835 | 918.5
8 | INS10002 | a) 11 KV Disc Insulators | 6 | 216 | Each | 1296 | -
| HWR00002 | b) 11KV metal parts | 6 | 82 | set | 492 | -
| FBE10022 | c) MS Stay Set with clamps | 4 | 448 | Each | 1792 | -
|  | Labour & Transport | - | - | - | - | 3856
9 |  | Coper cable 4 x 2.55 sqmm & GI pipe with bends etc for wiring | LS |  |  | 3300
10 |  | Plinth for distribution box | 1 | 3630 | - | 3630
10 |  | Sundries |  |  | LS | 2630
|  | Sub Total |  |  |  | 113091 | 25320 | 5385.2857
|  | 3% S &H Charges |  |  |  | 3392.73 |  | 107705.7143
|  | 3% Contingencies |  |  |  | 3392.73
|  | 10% Estt. & Genl. Charges |  |  |  | 11309.1
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  |  | 3129.552
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  |  | 253.2
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  |  | 1063
[6 empty] | 131185.56 | 29765.752
|  | Total |  |  |  | 160951.312

## P63
Estimate for erection of Terminal & Metering Arrangement for 33KV services with 33KV VCB
S.No. | Material code | Particulars | Qnty. | Rate | Per. | Amount
1 |  | Erection of 4 Pole structure
a | MST000229 | RS Joist 150 x 150 (6Nos) | 2 | 55347 | MT | 110694
b | MST00012 | MS Channel 100 x 50 mm | 1.3 | 53887 | MT | 70053.1
c | MST00015 | Ms Flat 75X8 & 50X8 mm | 0.5 | 53887 | MT | 26943.5
2 |  | Foundations
a |  | 33KV VCB Plinth erection | LS |  |  | 16516 | 18167.6
b |  | Structures | LS |  |  | 11434 | 12577.4
3 |  | Jumpers, connectors, insulators, Earth connections etc., | LS |  |  | 25410 | 27951
4 |  | Control cables, GI pipe with bends etc for wiring arrangements | LS |  |  | 19057 | 20962.7
5 |  | Fencing with gate | LS |  |  | 12705 | 13975.5
6 | BRK30002 | 33KV VCB with CTs & control pannel | 1 | 345256 | Each | 345256
7 | ABS30010 | 33 KV Isolators | 2 | 39800 | Each | 79600
8 | LAS00004 | 33 KV LAS | 3 | 4460 | Each | 13380
9 | ITR30072 | 33 KV CTs 0.2 class of accuracy | 3 | 20126 | Each | 60378
10 | ITR30012 | 33 KV PTs 0.2 class of accuracy | 3 | 21628 | Each | 64884
11 | MHT30021 | HT Trivector meter | 1 | 14338 | Each | 14338
12 | BAT00029 | 24 V 40 AH battery set including battery charger | 1 | 17000 | Each | 17000
13 | EMT00006 | CI Earth pipes | 8 | 2471 | Each | 19768
14 | BXS000174 | SMC DISTRIBUTION BOX | 1 | 13300 | Each | 13300
14a |  | Plinth for distribution Box | 1 | 3630 | Each | 3630
15 |  | Sundries | LS |  |  | 3150 | 675143
|  | TOTAL |  |  |  | 927496.6 | 20254.29 | 44166.5048
|  | 3 % S & H Charges |  |  |  | 27824.898 |  | 883330.0952
|  | 3 % Contingencies |  |  |  | 27824.898
|  | 10 % Estt. & Genrl. Charges |  |  |  | 92749.66
|  | Labour & Transport for all items except item No 2 & 14a |  |  |  | 164058 | 180463.8
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 20277.5688
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 1640.58
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 8686
|  | TOTAL ESTIMATE COST |  |  |  | 1270558.2048

## P(64-65)
Detailed Estimate For Erection of 33/11 KV Sub-Station
with (NT) X 5 MVA Power Transformers and NF = 3Nos. 11 KV feeders
(With 11kv 2 MVAR Capacitors Bank )
Sl. No. | Material code | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
1 |  | a) Lands and Rights | LS | As per local conditions | LS | 7
|  | b) Plantation of Trees | LS |  | LS | 0.2
2 |  | Control Room Cum section Office(including furniture) | LS |  | LS | 14
3 |  | Station Auxillaries
|  | a) Peripheral, Security Fencing, Approach road, retaing wall around switchward with gravel filling, gate and bore well | LS |  | LS | 9.2
|  | b) Yard Lighting | LS |  | LS | 0.5
|  | c) Fire Fighting Equipment | LS |  | LS | 0.4
|  | d) P&T Phone | LS |  | LS | 0.12
4 |  | Foundations for structures, PTRs & breakers | LS |  | LS | 3.8
5 |  | Busbar, Jumpers, Connectors Clamps etc., | LS |  | LS | 1.5
6 |  | Control Cables | LS |  | LS | 0.9
7 |  | Structural Steel | 15 | 0.553 | MT | 8.295
8 |  | Transformers
| PTR00006 | a) 33/11 KV 5 MVA Power Transformer | 1 | 33.454 | Each | 33.454
| DTC30001 | b) 11 kv /433 v 16 KVA Stn. Transformer | 1 | 0.697 | Each | 0.697
9 |  | Circuit Breakers (including Trivector Meter)
| BRK10002 | a) 11 kv Feeder VCB with CTs & Control panel (NF=3) | 3 | 2.455 | Each | 7.365
| BRK10004 | b) 11 kv LV VCB with CTs & Control panel | 1 | 2.785 | Each | 2.785
10 |  | Control Circuit panels
| OTH00057 | a) AC distribution Panel | 1 | 0.292 | Each | 0.292
| OTH00126 | b) DC annunciation panel | 1 | 0.124 | Each | 0.124
11 |  | Instrument Transformer
| ITR10020 | a) 11 KV P.T. 3 Phase | 1 | 0.183 | Each | 0.183
Sl. No. |  | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
12 |  | Lightining Arresstors
| LAS00004 | a) 33 KV 10KA | 6 | 0.046 | Each | 0.276
| LAS00001 | b) 11 KV Line Type (NF=3) | 9 | 0.015 | Each | 0.135
| LAS00002 | c) 11 KV Station Type 10 KA | 3 | 0.03 | Each | 0.09
13 |  | Isolating Switches
| ABS30010 | a) 33 KV 800 A AB Switch | 3 | 0.398 | Each | 1.194
| ABS10015 | b) 11 KV 800 A AB Switch (NT x 1+1) | 2 | 0.158 | Each | 0.316
| ABS10008 | c) 11 KV 400 A AB Switch (NF x 2+2) | 8 | 0.106 | Each | 0.848
| HGF30000 | d) 33 KV Horn Gap Fuse Set (1 x NT) | 1 | 0.07 | Set | 0.07
14 | CPT10013 | 2 MVAR 11 kv Capacitor Bank along with Associated Equipment | 1 | 10.132 | Each | 10.132
15 | BAT00029 | 24 V 40 AH battery set including battery charger | 2 | 0.17 | Each | 0.34
16 |  | Earthing of Power Transformer, VCBs, AB Switches, Structures with 75 x 8 mm G.I. Flat |  |  | LS | 2.05
|  | SUB TOTAL |  |  |  | 106.266 | 5.0603
101.2057
17 |  | Erection, Transport and commissioning charges on items No. 7 to 15 |  |  |  | 9.163 | 10.0793
18 |  | Contingencies on items 7 to 15 at 3% |  |  |  | 1.9979
19 |  | T & P Charges on Items No. 7 to 15 at 1% |  |  |  | 0.66596
20 |  | Establishment and General Charges at 10% |  |  |  | 10.6266
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 1.1325
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 0.09163
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 0.97
|  | TOTAL |  |  |  | 130.9136
|  | Or say (Rs.lakhs) |  |  |  | 130.91
Note : |  | NF=No. of 11 KV Feeders, The number of outgoing feeders at substation limited to the demand in MVA i.e. if substation demand is 5 MVA, the number of feeders should not exceed five.

## P(66-67)
Detailed Estimate For Erection of 33/11 KV Sub-Station
with (NT) X 5 MVA Power Transformers and NF = 2Nos. 11 KV feeders
(Without 11kv 2 MVAR Capacitors Bank)
Sl. No. | Material code | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
1 |  | a) Lands and Rights | LS | As per local conditions | LS | 7
|  | b) Plantation of Trees | LS |  | LS | 0.2
2 |  | Control Room Cum Section office (including furniture) | LS |  | LS | 14
3 |  | Station Auxillaries
|  | a) Peripheral, Security Fencing, Approach road, retaing wall around switchward with gravel filling, gate and bore well | LS |  | LS | 9.2
|  | b) Yard Lighting | LS |  | LS | 0.5
|  | c) Fire Fighting Equipment | LS |  | LS | 0.4
|  | d) P&T Phone | LS |  | LS | 0.12
4 |  | Foundations for structures, PTRs & breakers | LS |  | LS | 3.8
5 |  | Busbar, Jumpers, Connectors Clamps etc., | LS |  | LS | 1.5
6 |  | Control Cables | LS |  | LS | 0.9
7 |  | Structural Steel | 15 | 0.553 | MT | 8.295
8 |  | Transformers
| PTR00006 | a) 33/11 KV 5 MVA Power Transformer | 1 | 33.454 | Each | 33.454
| DTC30001 | b) 11 kv /433 v 16 KVA Stn. Transformer | 1 | 0.697 | Each | 0.697
9 |  | Circuit Breakers (including Trivector Meter)
| BRK10002 | a) 11 kv Feeder VCB with CTs & Control panel (NF=2) | 2 | 2.455 | Each | 4.91
| BRK10004 | b) 11 kv LV VCB with CTs & Control panel | 1 | 2.785 | Each | 2.785
10 |  | Control Circuit panels
| OTH00057 | a) AC distribution Panel | 1 | 0.292 | Each | 0.292
| OTH00126 | b) DC annunciation panel | 1 | 0.124 | Each | 0.124
11 |  | Instrument Transformer
| ITR10020 | a) 11 KV P.T. 3 Phase | 1 | 0.183 | Each | 0.183
Sl. No. |  | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
12 |  | Lightining Arresstors
| LAS00004 | a) 33 KV 10KA | 6 | 0.046 | Each | 0.276
| LAS00001 | b) 11 KV Line Type (NF=3) | 6 | 0.015 | Each | 0.09
| LAS00002 | c) 11 KV Station Type 10 KA | 3 | 0.03 | Each | 0.09
13 |  | Isolating Switches
| ABS30010 | a) 33 KV 800 A AB Switch | 3 | 0.398 | Each | 1.194
| ABS10015 | b) 11 KV 800 A AB Switch (NT x 1+1) | 2 | 0.158 | Each | 0.316
| ABS10008 | c) 11 KV 400 A AB Switch (NF x 2+2) | 6 | 0.106 | Each | 0.636
| HGF30000 | d) 33 KV Horn Gap Fuse Set (1 x NT) | 1 | 0.07 | Set | 0.07
14 | BAT00029 | 24 V 40 AH battery set including battery charger | 2 | 0.17 | Each | 0.34
15 |  | Earthing of Power Transformer, VCBs, AB Switches, Structures with 75 x 8 mm G.I. Flat |  |  | LS | 2.05
|  | SUB TOTAL |  |  |  | 93.422 | 4.4487
88.9733
17 |  | Erection, Transport and commissioning charges on items No. 7 to 15 |  |  |  | 7.681 | 8.4491
18 |  | Contingencies on items 7 to 15 at 3% |  |  |  | 1.6741
19 |  | T & P Charges on Items No. 7 to 15 at 1% |  |  |  | 0.55802
20 |  | Establishment and General Charges at 10% |  |  |  | 9.3422
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 0.94476
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 0.07681
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 0.85
|  | TOTAL |  |  |  | 114.5489
|  | Or say (Rs.lakhs) |  |  |  | 114.55
Note : |  | NF=No. of 11 KV Feeders, The number of outgoing feeders at substation limited to the demand in MVA i.e. if substation demand is 5 MVA, the number of feeders should not exceed five.

## P(68-69)
Detailed Estimate For Erection of 33/11 KV Sub-Station
with (NT) X 5 MVA Power Transformers and NF = 3Nos. 11 KV feeders
(Without 11kv 2 MVAR Capacitors Bank)
Sl. No. | Material code | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
1 |  | a) Lands and Rights | LS | As per local conditions | LS | 7
|  | b) Plantation of Trees | LS |  | LS | 0.2
2 |  | Control Room Cum Section office (including furniture) | LS |  | LS | 14
3 |  | Station Auxillaries
|  | a) Peripheral, Security Fencing, Approach road, retaing wall around switchward with gravel filling, gate and bore well | LS |  | LS | 9.2
|  | b) Yard Lighting | LS |  | LS | 0.5
|  | c) Fire Fighting Equipment | LS |  | LS | 0.4
|  | d) P&T Phone | LS |  | LS | 0.12
4 |  | Foundations for structures, PTRs & breakers | LS |  | LS | 3.8
5 |  | Busbar, Jumpers, Connectors Clamps etc., | LS |  | LS | 1.5
6 |  | Control Cables | LS |  | LS | 0.9
7 |  | Structural Steel | 15 | 0.553 | MT | 8.295
8 |  | Transformers
| PTR00006 | a) 33/11 KV 5 MVA Power Transformer | 1 | 33.454 | Each | 33.454
| DTC30001 | b) 11 kv /433 v 16 KVA Stn. Transformer | 1 | 0.697 | Each | 0.697
9 |  | Circuit Breakers (including Trivector Meter)
| BRK10002 | a) 11 kv Feeder VCB with CTs & Control panel (NF=3) | 3 | 2.455 | Each | 7.365
| BRK10004 | b) 11 kv LV VCB with CTs & Control panel | 1 | 2.785 | Each | 2.785
10 |  | Control Circuit panels
| OTH00057 | a) AC distribution Panel | 1 | 0.292 | Each | 0.292
| OTH00126 | b) DC annunciation panel | 1 | 0.124 | Each | 0.124
11 |  | Instrument Transformer
| ITR10020 | a) 11 KV P.T. 3 Phase | 1 | 0.183 | Each | 0.183
Sl. No. |  | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
12 |  | Lightining Arresstors
| LAS00004 | a) 33 KV 10KA | 6 | 0.046 | Each | 0.276
| LAS00001 | b) 11 KV Line Type (NF=3) | 9 | 0.015 | Each | 0.135
| LAS00002 | c) 11 KV Station Type 10 KA | 3 | 0.03 | Each | 0.09
13 |  | Isolating Switches
| ABS30010 | a) 33 KV 800 A AB Switch | 3 | 0.398 | Each | 1.194
| ABS10015 | b) 11 KV 800 A AB Switch (NT x 1+1) | 2 | 0.158 | Each | 0.316
| ABS10008 | c) 11 KV 400 A AB Switch (NF x 2+2) | 8 | 0.106 | Each | 0.848
| HGF30000 | d) 33 KV Horn Gap Fuse Set (1 x NT) | 1 | 0.07 | Set | 0.07
14 | BAT00029 | 24 V 40 AH battery set including battery charger | 2 | 0.17 | Each | 0.34
15 |  | Earthing of Power Transformer, VCBs, AB Switches, Structures with 75 x 8 mm G.I. Flat |  |  | LS | 2.05
|  | SUB TOTAL |  |  |  | 96.134 | 4.5778
91.5562
17 |  | Erection, Transport and commissioning charges on items No. 7 to 15 |  |  |  | 8.038 | 8.8418
18 |  | Contingencies on items 7 to 15 at 3% |  |  |  | 1.7554
19 |  | T & P Charges on Items No. 7 to 15 at 1% |  |  |  | 0.58514
20 |  | Establishment and General Charges at 10% |  |  |  | 9.6134
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 0.9935
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 0.08038
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 0.87
|  | TOTAL |  |  |  | 118.0698
|  | Or say (Rs.lakhs) |  |  |  | 118.07
Note : |  | NF=No. of 11 KV Feeders, The number of outgoing feeders at substation limited to the demand in MVA i.e. if substation demand is 5 MVA, the number of feeders should not exceed five.

## P(70-71)
Detailed Estimate For Erection of 33/11 KV Sub-Station
with (NT) X 5 MVA Power Transformers and NF = 4 Nos. 11 KV feeders
(Without 11kv 2 MVAR Capacitors Bank )
Sl. No. | Material code | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
1 |  | a) Lands and Rights | LS | As per local conditions | LS | 7
|  | b) Plantation of Trees | LS |  | LS | 0.2
2 |  | Control Room Cum Section office (including furniture) | LS |  | LS | 14
3 |  | Station Auxillaries
|  | a) Peripheral, Security Fencing, Approach road, retaing wall around switchward with gravel filling, gate and bore well | LS |  | LS | 9.2
|  | b) Yard Lighting | LS |  | LS | 0.5
|  | c) Fire Fighting Equipment | LS |  | LS | 0.4
|  | d) P&T Phone | LS |  | LS | 0.12
4 |  | Foundations for structures, PTRs & breakers | LS |  | LS | 3.8
5 |  | Busbar, Jumpers, Connectors Clamps etc., | LS |  | LS | 1.5
6 |  | Control Cables | LS |  | LS | 0.9
7 |  | Structural Steel | 15 | 0.553 | MT | 8.295
8 |  | Transformers
| PTR00006 | a) 33/11 KV 5 MVA Power Transformer | 1 | 33.454 | Each | 33.454
| DTC30001 | b) 11 kv /433 v 16 KVA Stn. Transformer | 1 | 0.697 | Each | 0.697
9 |  | Circuit Breakers (including Trivector Meter)
| BRK10002 | a) 11 kv Feeder VCB with CTs & Control panel (NF=4) | 4 | 2.455 | Each | 9.82
| BRK10004 | b) 11 kv LV VCB with CTs & Control panel | 1 | 2.785 | Each | 2.785
10 |  | Control Circuit panels
| OTH00057 | a) AC distribution Panel | 1 | 0.292 | Each | 0.292
| OTH00126 | b) DC annunciation panel | 1 | 0.124 | Each | 0.124
11 |  | Instrument Transformer
| ITR10020 | a) 11 KV P.T. 3 Phase | 1 | 0.183 | Each | 0.183
Sl. No. |  | Particulars | Qty. | Rate (Rs. in lakhs) | Unit | Amount (Rs. in lakhs)
12 |  | Lightining Arresstors
| LAS00004 | a) 33 KV 10KA | 6 | 0.046 | Each | 0.276
| LAS00001 | b) 11 KV Line Type (NF=4) | 12 | 0.015 | Each | 0.18
| LAS00002 | c) 11 KV Station Type 10 KA | 3 | 0.03 | Each | 0.09
13 |  | Isolating Switches
| ABS30010 | a) 33 KV 800 A AB Switch | 3 | 0.398 | Each | 1.194
| ABS10015 | b) 11 KV 800 A AB Switch (NT x 1+1) | 2 | 0.158 | Each | 0.316
| ABS10008 | c) 11 KV 400 A AB Switch (NF x 2+2) | 10 | 0.106 | Each | 1.06
| HGF30000 | d) 33 KV Horn Gap Fuse Set (1 x NT) | 1 | 0.07 | Set | 0.07
14 | BAT00029 | 24 V 40 AH battery set including battery charger | 2 | 0.17 | Each | 0.34
15 |  | Earthing of Power Transformer, VCBs, AB Switches, Structures with 75 x 8 mm G.I. Flat |  |  | LS | 2.05
|  | SUB TOTAL |  |  |  | 98.846 | 4.707
94.139
17 |  | Erection, Transport and commissioning charges on items No. 7 to 15 |  |  |  | 8.397 | 9.2367
18 |  | Contingencies on items 7 to 15 at 3% |  |  |  | 1.8368
19 |  | T & P Charges on Items No. 7 to 15 at 1% |  |  |  | 0.61226
20 |  | Establishment and General Charges at 10% |  |  |  | 9.8846
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 1.0379
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 0.08397
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 0.9
|  | TOTAL |  |  |  | 121.5985
|  | Or say (Rs.lakhs) |  |  |  | 121.6
Note : |  | NF=No. of 11 KV Feeders, The number of outgoing feeders at substation limited to the demand in MVA i.e. if substation demand is 5 MVA, the number of feeders should not exceed five.

## 11KV Bay-72
Cost data for erection of 11KV Bay extension alon with VCB in existing 33/11KV Sub-Station (with RS Joists)
S.No. | Material code | Particulars | Qnty. | Rate | Per. | Amount
1 | MST00029 | 150 x 150Sq.mm H Type beam of 9.0mts length (2Nos RS Joists) | 0.83 | 55347 | MT | 45938.01
2 | MST00012 | 100 x 50Sq.mm Channel | 0.5 | 53887 | MT | 26943.5
3 | MST00015 | MS Flat 75 x 8mm | 0.3 | 53887 | MT | 16166.1
4 | MST00002 | MS Angle 50x50x6mm | 0.1 | 53887 | MT | 5388.7
5 | ABS10008 | AB Switch 400Amps converntional type | 2 | 10623 | Each | 21246 | 2184
6 | CDR00005 | 200Sq.mm ACSR Conductor (Panther conductor) | 0.05 | 132334 | Km | 6616.7
7 | BRK10002 | 11 kv Feeder VCB with CTs & Control panel | 1 | 245528 | Each | 245528 | 13418
8 | LAS00002 | 11KV Lightining Arrestors station type | 3 | 2977 | Each | 8931
9 | INS10008 | 11KV post type insulators | 12 | 233 | Each | 2796
10 | BAT00029 | 24V 40AH Battery with trickle charger | 1 | 17000 | Each | 17000
11 | INS10003 | 11KV Polymer insulators | 6 | 196 | Each | 1176
12 | HWR 00002 | 11KV Metal Parts | 6 | 82 | Each | 492
13 | CBP00002 | LT PVC CU Control cable 4 core 2.5 sqmm | 50 | 68 | M | 3400
14 | CBP00006 | LT PVC CU Control cable 10 core 2.5 sqmm | 50 | 165 | M | 8250
15 | EMT00006 | CI Earth pipe | 3 | 2471 | M | 7413 | 1911
16 | BNT00026 | MS Bolts &nuts 5/8"x4" | 50 | 81 | KG | 4050
17 |  | Plinth for VCB |  |  |  | 12000
18 |  | Earthing arrangments (20mts length with 75 x 8 MS flat) | LS |  |  | 6600
19 |  | Pad clamps, bolt & nuts & Miscellaneous items | LS |  |  | 1920
|  | TOTAL |  |  |  | 441855.01 | 17513 | 21040.7148
420814.2952
|  | 3% storage & handling charges on items (1) to (16) |  | 421335.01 |  | 12640.0503
|  | 3 % Contingencies |  |  |  | 13255.6503
|  | 10 % Estt. & Genrl. Charges |  |  |  | 44185.501
|  | Labour & Transport |  |  |  | 36300 | 39930
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 4486.68
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 363
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 4205
|  | TOTAL ESTIMATE COST |  |  |  | 557290.8916

## 33KV Bay-73
Cost data for erection of 33KV Bay extension in existing 33/11KV Sub-Station (with RS Joists)
S.No. | Material code | Particulars | Qnty. | Rate | Per. | Amount
1 | MST00029 | 150 x 150Sq.mm H Type beam of 9.0mts length (2Nos RS Joists) | 0.83 | 55347 | MT | 45938.01 | 1406
2 | MST00012 | 100 x 50Sq.mm Channel | 0.5 | 53887 | MT | 26943.5 | 5516
3 | MST00015 | MS Flat 75 x 8mm | 0.4 | 53887 | MT | 21554.8 | 500
4 | ABS30010 | AB Switch 800Amps converntional type | 1 | 39800 | Each | 39800 | 1457
5 | CDR00005 | 200Sq.mm ACSR Conductor (Panther conductor) | 0.02 | 132334 | Km | 2646.68 | 1200
6 | INS30006 | 33KV Disc Insulators | 6 | 391 | Each | 2346 | 360
7 | HWR 00004 | 33KV Metal Parts | 6 | 180 | Each | 1080 | 10439 | 12004.85
8 |  | Earthing arrangments (20mts length with 75 x 8 MS flat) | LS |  |  | 6600
9 |  | Miscelleneous items like fabrication of channels & Pad clamps etc., | LS |  |  | 3000
|  | TOTAL |  |  |  | 149908.99 | 7138.5233
|  | 3% storage & handling charges on items (1) to (7) |  | 149908.99 |  | 4497.2697 | 142770.4667
|  | 3 % Contingencies |  |  |  | 4497.2697
|  | 10 % Estt. & Genrl. Charges |  |  |  | 14990.899
|  | Labour & Transport |  |  |  | 14520 | 15972
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 1794.672
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 145.2
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 1428
|  | TOTAL ESTIMATE COST |  |  |  | 191782.3004

## PTR erection-74
Cost data for erection of 5.0MVA additional PTR with 33KV Bay extension in existing 33/11KV Sub-Station.
S.No. | Material code | Particulars | Qnty. | Rate | Per. | Amount
1 | MST00029 | 150 x 150Sq.mm RS Joists | 0.8 | 55347 | MT | 44277.6 | 1406
2 | MST00012 | 100 x 50Sq.mm Channel | 0.5 | 53887 | MT | 26943.5 | 5516
3 | MST00015 | MS Flat 75 x 8mm | 0.4 | 53887 | MT | 21554.8 | 500
4 | ABS30010 | AB Switch 800Amps converntional type | 1 | 39800 | Each | 39800 | 1457
5 | CDR00005 | 200Sq.mm ACSR Conductor (Panther conductor) | 0.05 | 132334 | Km | 6616.7 | 1500
6 | INS30006 | 33KV Disc Insulators | 6 | 391 | Each | 2346 | 360
7 | HWR 00004 | 33KV Metal Parts | 6 | 180 | Each | 1080
8 | PTR00006 | 33/11KV 5.0MVA PTR | 1 | 3345440 | Each | 3345440 | 21075
9 | HGF30000 | 33KV 3-Ph HG Fuse Set | 1 | 7004 | Each | 7004 | 555
10 | EMT00006 | CI Earth pipes | 4 | 2471 | Each | 9884 | 2548
11 |  | Earthing arrangments (20mts length with 75 x 8 MS flat) | LS |  |  | 6600 | 34917
12 |  | Miscelleneous items like fabrication of channels & Pad clamps & T Clamps etc., | LS |  |  | 6000
13 |  | Plinth for PTR | LS |  |  | 80000
|  | TOTAL |  |  |  | 3597546.6 | 171311.7429
|  | 3% storage & handling charges on items (1) to (9) |  | 3504946.6 |  | 105148.398 | 3426234.8571
|  | 3 % Contingencies |  |  |  | 107926.398
|  | 10 % Estt. & Genrl. Charges |  |  |  | 107926.398
|  | Labour & Transport |  |  |  | 48400 | 53240
|  | Service Tax @ 12.36% on Labour & Transport |  |  |  | 5982.24
|  | BW Welfare cess @ 1% on Labour & Transport |  |  |  | 484
|  | BW Welfare cess @ 1% on cost of material (Ex. VAT) |  |  |  | 34260
|  | TOTAL ESTIMATE COST |  |  |  | 4007674.034

## P-75
REC - Construction Standard Nos. Other than the Items Included in the 33 KV
11 KV & LT Lines erection and Centralised Material
Sl. No. | Particulars | REC Construction Standard No./ Specification No. | Remarks / Notes
1 | 1.53 Mts. Cross arm (Channel) | M-1/1981 | 33 KV line
2 | Top clamp with cleat | M-4/1984 | 33 KV line
3 | Back clamp | K-1/1972 | 33 KV line & 11 KV line
4 | Base concreting | K-2/1972 (R-1987) | 33 KV line & 11 KV line
5 | Stay sets complete with concreting | G-1/1972 | 33 KV line & 11 KV line
6 | Coil earthing | J-1/1972 | 33 KV line & 11 KV line
7 | Pipe earthing | J-2/1972 | 33 KV line & 11 KV line
8 | Concreting of poles | K-1/1972 | All lines
9 | 8 M PSCC poles | 15/1979 | 11 KV line
10 | 1.07 M Cross arm (Channel) | A-6/1972 | 11 KV line
11 | Top clamp with cleat | A-7/1972 | 11 KV line
12 | Bracing set with double cross arm | A-12/1972 | H.T. line
13 | Guy grip dead end | G-1/1972 & SP.No.25/1983 | H.T. line
14 | C.I. Knob | 31/1983 | L.T lines
15 | L.T. conductor dead end | G-2/1984 | L.T lines
16 | Guy grip dead end | G-2/1984 | L.T lines
17 | L.T. Spares | 29/1983 (R-1987) | L.T lines
18 | Spool for shackle insulator tieing | D-6/1984 | L.T lines
19 | D.P. Structure for distribution substation | F-1/1981 (R-1993) | L.T lines
20 | HT & LT conductor dead end fittings | Sp. No.25/1983 | All lines
21 | Side tie for pin insulator tieing | - do - | All lines
22 | Fibre Reinforced Plastic Cross Arms | 40/1987 | 11KV &LT lines

## P-76
COST OF FABRICATED MATERIALS
Sl. No. | Material code | Particulars |  |  |  | Unit | Rate
1 | PLS00001 | 8.0mts PSCC Poles 140 Kgs. WL |  |  |  | Each | 1875
2 | PLS00002 | 8.0mts PSCC Poles 200 Kgs. WL |  |  |  | Each | 1995
3 | PLS00004 | 9.1 M PSCC Poles 280 Kgs. WL |  |  |  | Each | 3640
4 |  | RCC Base Plates |  |  |  | Each | 100
5 | FBE30009 | MS Stay sets without base plates with 20 mm rod and channel |  |  |  | Each | 366
6 | FBE10010 | MS Stay sets without base plates with 16 mm rod and channel |  |  |  | Each | 385
7 | FBE00026 | 33 KV 'V' cross arms 1.53 M |  |  |  | Each | 1112
8 | FBE10001 | 11 KV 'V' cross arms 65 x 65 x 6 mm MS angle |  |  |  | Each | 478
9 | BXS00147 | Moulded Box for Single & 3-Ph Meters. |  |  |  | Each | 433
10 | FBE00008 | L.T. 3 phase 5 wire Cross Arm 1.30 Mts. Long
|  | with 65 x 65 x 6 MS Angle |  |  |  | Each | 381
11 | FBE00020 | L.T. 3 phase 4 wire Cross Arm 1.30 Mts. Long
|  | with 65 x 65 x 6 MS Angle |  |  |  | Each | 247
12 |  | Single phase Cross arms 50 x 50 x 6 mm Angle |  |  |  | Each | 206
12 | FBE00040 | Back clamps 75 x 8 MS Flat |  |  |  | Each | 98
12a | FBE00001 | Back clamps 50 x 6 MS Flat |  |  |  | Each | 72
13 | FBE00038 | Stay clamps 50 x 6mm MS Flat |  |  |  | Each | 72
13a | FBE00019 | Stay clamps 75 x 8mm MS Flat |  |  |  | Each | 72
14 | FBE30006 | 33 KV Top Clamp with cleat |  |  |  | Each | 519
15 | FBE10007 | 11 KV Top Clamp with cleat |  |  |  | Each | 281
16 | FBE00041 | L.T. Back Clamp |  |  |  | Each | 72
| AE/Comml | ADE/Comml | DE/Comml | GM/Planning | CGM/Operation | CGM/Finance
|  | Director/Operation |  | Directro/Proj & Fin
Chairman & Managing Director