SOUTHERN POWER DISTRIBUTION COMPANY OF A.P. LIMITED

TIRUPATI

(A Govt. of Andhra Pradesh Undertaking)

DESIGN, SUPPLY, INSTALLATION, TESTING, COMMISSIONING WITH FIVE YEARS OF COMPREHENSIVE MAINTENANCE CONTRACT OF 100 KWp SOLAR PHOTOVOLTAIC POWER PLANT ON THE ROOF TOP OF VIDYUTH NILAYAM, APSPDCL, TIRUPATI, AP

PART-I (TECHNICAL BID)

BID DOCUMENT No. CGM/PROJECTS/APSPDCL/SIP- 01/2013-14

The Chief General Manager/ Projects				Phones:

SPDC of A.P. Ltd., 19-13-65/A					Fax 	: 0877-2284105

Near Srinivasa Kalyanamandapams,				Mobile: 9440812366

Tiruchanur Road

Tirupati–517 503

SOUTHERN POWER DISTRIBUTION COMPANY OF A.P. LTD

TIRUPATI

INVITATION FOR BIDS (IFB)

(LOCAL COMPETITITVE BIDDING)

Bid No. CGM/PROJECTS/APSPDCL /SIP- 01  /2013-14

1.	APSPDCL invites sealed bids under Local Competitive Bidding (LCB) from eligible bidders for Design, Supply, Installation, Testing, Commissioning With Five Years of Comprehensive Maintenance Contract of 100 Kwp Solar Photovoltaic Power Plant on the Roof -top of Vidyuth Nilayam, APSPDCL, Tirupati, Chittoor District, Andhra Pradesh

- Brief description of “the works” is as follows:

| Sub-Project No. | District | Name of the work | Completion Period | Bid security (2%) Rs. in lakhs |
| --- | --- | --- | --- | --- |
| CGM/PROJECTS/ APSPDCL/ SIP-01 / 2013-14 | Chittoor | Design, Supply, Installation, Testing, Commissioning With Five Years of Comprehensive Maintenance Contract of 100 Kw Solar Photovoltaic Power Plant on the Roof -top of Vidyuth Nilayam, APSPDCL, Tirupati, Chittoor District, Andhra Pradesh | Three months | 2.06 |

3. (a)	All the interested bidders may visit www.eprocurement.gov.in to view and download the tender documents free-of-cost from 02.05.13 at 22:00 Hrs. to 23.05.13 upto 12:00 Hrs.

3. (b)	Request for sending bid documents by post will not be entertained.

4.	Those who are interested to submit bids will have to register in the above mentioned site and also have to obtain Digital Certificates. The details and procedure for obtaining digital certificate are mentioned in the website or contact the helpdesk of the site.

5.0	ELIGIBILITY AND QUALIFICATION OF INTENDED BIDDERS

5.1	The intending bidders shall inter-alia meet the following conditions to qualify for the award of contract.

1.1	Only MNRE approved organizations/ channel partners of ratings of 1A/ 1B/ PSU’s, who have got their products tested and qualified by any of the three authorized test centers and who have submitted information to the test centre about the company along with a copy to the Ministry in the MNRE format will be eligible to participate.

1.2	The firm must have valid EPF/Service Tax/STCC/ VAT clearance certificate. (Pl. attach copy of valid STCC/ VAT clearance certificate)

1.3	Having achieved a minimum annual financial turn-over of Rs 5.00 crores in any one of the last five year exclusively in the business of solar PV alone.

(Pl. attach copy of audited balance sheet for 2008-09, 2009-10, 2010-11 and 2011-12 and 2012-13)

  - The firm must have designed, manufactured, tested supplied, erected, commissioned minimum capacity of 500 KW (Cumulative over the period of last three years) in the range of 10 kW and above and which is/are in successful operation on the date of bid opening.

(Pl attach copies of PO’s and satisfactory report from previous installations in support of the same)

1.5	The firm must have set up at least one solar power plant of 50 KW or above capacity in the   premises of  reputed  Government/Private  buildings  (or)

Grid interactive solar power developers of 1 MW size or above with proven experience may also participate in tenders

(Pl attach copies of PO’s and satisfactory report from previous installations in support of the same)

1.6	The firm must have adequate capacity to design, manufacture, test , supply, erect, and commission the power plant within the given time schedule.

(Pl furnish a brief write-up, backed with adequate data, explaining the available capacity and experience (both technical and commercial) for the manufacture and supply of the required systems and equipment within the specified time of completion after meeting all their current commitments.)

1.7	The products must conform to minimal technical requirements/ standards for off grid/standalone/grid connected solar PV power plants /systems to be deployed under the Jawaharlal Nehru National Solar Mission.

(Pl. attach copies of recent test certificates from SEC/ other authorized Test Centres of MNRE, GOI as proof thereof)

1.8	The  products/  systems/  devices  quoted  in  tender  should  be  as  per  MNRE specifications.

1.9	All above criteria should be strictly followed.	Tenderer should quote only if he is eligible..

6.0	BID SECURITY

6.1      The Bid Security an amount of Rs 2.06 Lakhs shall have to be submitted in original in the form of Demand Draft in favour of Accounts Officer/ CPR/ APSPDCL/ Tirupati payable at Tirupati issued on or after 03.05.13 quoting proper Bid Reference No. and other relevant details as required in the bid. The bid security shall be from any scheduled Bank only.

7.0	BID PRICE

The bid price shall have to be in Indian Rupees (INR) only.

8.0	APSPDCL reserves the right to cancel/withdraw the IFB without assigning any reason for such decision. Such decision will not incur any liability whatsoever on the part of APSPDCL consequently.

9.0	Alternative Bids will not be considered.

CORPORATE OFFICE : APSPDCL

BID No : CGM/PROJECTS/APSPDCL/ SIP-  01 /2013-14

| Notice Inviting Tender Details |  |  |
| --- | --- | --- |
| S.No | Description |  |
| 1 | Department Name | Southern Power Distribution Company of A.P. Ltd., (A.P.S.P.D.C.L.) |
| 2 | Office | Chief General Manager, Projects, Corporate Office, APSPDCL, Tirupati. |
| 3 | Bid Number | CGM/PROJECTS/APSPDCL/SIP- 01 /2013-14 |
| 4 | Tender Subject | Design, Supply, Installation, Testing, Commissioning With Five Years of Comprehensive Maintenance Contract of 100 Kwp Solar Photovoltaic Power Plant on the Roof -top of Vidyuth Nilayam, APSPDCL, Tirupati, AP |
| 5 | Period of work | Within Three months from the date of issue of notice to proceed with the work |
| 6 | Tender Type | Open |
| 7 | Tender Category | Works (System improvement project works ) |
| 8 | Bid Security (INR) | Rs.2.06 Lakhs |
| 9 | Bid Security Payable to | The Bid Security shall have to be submitted in original in the form of Demand Draft only in favour of Accounts Officer/ CPR/ APSPDCL/ Tirupati payable at Tirupati issued on or after 3.05.2013 quoting proper Bid Reference No. and other relevant details as required in the bid. The bid security shall be from any scheduled Bank only. |
| 10 | Transaction Fee | The participating bidder has to pay transaction fee @ 0.03% of E.C.V for all works with E.C.V up to Rs.50 Crores, in favour of A.P.Technological services, Government of Andhra Pradesh, Hyderabad mandatorily through the electronic payment gateway as per G.O.Ms. No.13, Dt.5.7.06. The participating bidder has to pay @ 10.30% levied by Government of India towards Service Tax on the above transaction fee in favour of A.P.Technological services, Government of Andhra Pradesh, Hyderabad through the electronic payment gateway as per G.O.MS. No.13, dt.5.7.06. Corpus Fund: In addition, the successful bidder has to pay @ 0.04% of E.C.V with a cap of Rs.10,000/- at the time of agreement, towards e-procurement corpus fund in the shape of D.D in favour of A.P.Technological services, Government of Andhra Pradesh, Hyderabad. |
| 11 | Transaction Fee Payable to | A.P.Technological services, Government of Andhra Pradesh, Hyderabad |
| 12 | Schedules downloading start date on line | 02.05.2013 from 22:00 hrs. |
| 13 | Schedules downloading closing date on line | 23.05.2013 Upto 12:00 hrs. |
| 14 | Bid Submission closing date on line | 24.05.2013 upto 15:00 hrs. |
| 15 | Last date for submission of hard copies along with DD towards Bid Security to reach the Employer | 27.05.2013 upto 12:00 hrs. |
| 16 | Bid submission | On Line through www.eprocurement.gov.in. |
| 17 | Pre-Qualification & Technical Bid Opening Date (Qualification and Eligibility Stage and Technical Bid Stage) | On 27.05.2013 at 15:00 Hrs. |
| 18 | Price Bid Opening Date (Financial Bid Stage) | On or after 3.06.2013 at 12:00 Hrs. |
| 19 | Place of Tender Opening | O/o. CGM/ Projects/ Corporate Office, APSPDCL, Tirupati |
| 20 | Officer Inviting Bids/ Contact Person+ | Chief General Manager / Projects / APSPDCL |
| 21 | Address/E-mail id | Chief General Manager / Projects/ Corporate Office/ APSPDCL, 19-13-65/A, Near Srinivasa kalyana mandapam, Tiruchanur Road, Tirupati. cgmprojects@gmail.com & cgm_proj@southernpower.ap.co.in |
| 22 | Contact Details/Telephone, Fax | Cell No 9440812366 Fax No.0877-2284105 |
| 23 | Eligibility Criteria | 1.1 Only MNRE approved organizations/ channel partners of ratings of 1A/ 1B/ PSU’s, who have got their products tested and qualified by any of the three authorized test centers and who have submitted information to the test centre about the company along with a copy to the Ministry in the MNRE format will be eligible to participate. 1.2 The firm must have valid EPF/Service Tax/STCC/ VAT clearance certificate. 1.3 Having achieved a minimum annual financial turn-over of Rs 5.00 crores in any one of the last five year exclusively in the business of solar PV alone. - The firm must have designed, manufactured, tested supplied, erected, commissioned minimum capacity of 500KW (Cumulative over the period of last three years) in the range of 10 kW and above and which is/are in successful operation on the date of bid opening. 1.5 The firm must have set up at least one solar power plant of 50 KW or above capacity in the premises of reputed Government/Private buildings (or) Grid interactive solar power developers of 1 MW size or above with proven experience may also participate in tenders. 1.6 The firm must have adequate capacity to design , manufacture, test , supply, erect, and commission the power plant within the given time schedule. 1.7 The products must conform to minimal technical requirements/ standards for off grid/standalone/ grid connected solar PV power plants /systems to be deployed under the Jawaharlal Nehru National Solar Mission. 1.8The products/ systems/ devices quoted in tender should be as per MNRE specifications. 1.9 All above criteria should be strictly followed. Tenderer should quote only if he is eligible. |
| 24 | Procedure for Bid Submission | - Bids shall be submitted online on www.eprocurement.gov.in platform The participating bidders in the tender should register themselves free of cost on e-procurement platform in the website www.eprocurement.gov.in. ii) Bidders can log-in to e-procurement platform in Secure mode only by signing with the Digital certificates. - The bidders who are desirous of participating in e-procurement shall submit their technical bids, price bids as per the standard formats available at the e-market place. - The bidders should scan and upload the copies of all the following documents in support of technical & price bids in proof of qualification requirement duly signing on all the statements, documents & certificates uploaded by him, owning responsibility for their correctness/authenticity: S. No.; Description. Documents to be uploaded on-line as part of Technical bid proposal. 1; Technical experience certificates issued by competent authority along with POs, agreements. 2; Financial certificates for the last five years in proof of turn-over, Balance sheets, Profit & Loss A/c statements, Income Tax documents. 3; Demand Draft towards Bid security from any schedule Bank. 4; Annexures I to VII. 5; Test certificates issued by MNRE/Approved MNRE test centres. 6; Minimum guaranteed generation. 7; Brief write-up, backed with adequate data, explaining the available capacity and experience (both technical and commercial) for the manufacture and supply of the required systems. 8; Copy of EPF/Service Tax/STCC/ PAN/VAT clearance certificate.. 9; Any other documents if required. v) For each uploaded document on line, the bidder should provide the index of the file names and its contents invariably. |
|  |  | vi) After uploading the documents, copies of all the uploaded statements, certificates, documents along with the original Demand Draft in respect of Bid Security (except the Price bid / offer) are to be submitted by the bidder to the Chief General Manager / Projects/ APSPDCL, Tirupati so as to reach before the date and time of opening of the technical bid. The Department shall not hold any risk on account of postal delay. Similarly, if any of the certificates, documents, etc., furnished by the bidder are found to be false/fabricated/ bogus, the bidder will be disqualified, blacklisted and action will be initiated as deemed fit and the Bid Security will be forfeited. vii) The department will not hold any risk and responsibility regulating non-visibility of the scanned and uploaded documents. viii) The Documents that are uploaded online on e-market place will only be considered for Technical Bid Evaluation. ix) Hard copies received after the deadline date & time, prescribed in bid even though the bidder uploads the bid in the e-procurement platform will be summarily rejected treating them as late bids and/or returned unopened to the bidder. x) Important Notice to Contractors, Suppliers and Department users: In the endeavor to bring total automation of processes in e-Procurement, the Govt. has issued orders vide G.O.Ms.No. 13 dated. 5.7.2006 permitting integration of electronic Payment Gateway of ICICI/HDFC Banks with e-Procurement platform, which provides a facility to participating suppliers/contractors to electronically pay the transaction fee online using their credit cards. |
| 25 | Rights reserved with the Department | APSPDCL reserves the right to accept or reject any or all of the tender bids received without assigning any reasons therefore. The APSPDCL also reserves the right to split the tender and place contract on more than one bidder at its discretion. |
| 26 | General Terms and Conditions | As per the tender bid documents. |

CHIEF GENERAL MANAGER/ PROJECTS

APSPDCL, Corporate Office, 19-13-65/A,

Near Srinivasakalyanamandapams,

Tiruchanur Road, Tirupati

Mobile: 9440812366

#### Fax No.0877-2284105

INSTRUCTIONS TO BIDDERS (ITB)

DETAILED TENDER NOTICE

Name of Work :	 Design, Supply, Installation, Testing, Commissioning With Five Years of Comprehensive Maintenance Contract of 100	kWp Solar Photovoltaic Power Plant on the roof top of Vidyuth Nilayam in APSPDCL, Tirupati

1.	ELIGIBILITY CRITERIA

1.1	Only MNRE approved organizations/ channel partners of ratings of 1A/ 1B/ PSU’s, who have got their products tested and qualified by any of the three authorized test centers and who have submitted information to the test centre about the company along with a copy to the Ministry in the MNRE format will be eligible to participate.

1.2	The firm must have valid EPF/Service Tax/STCC/ VAT clearance certificate. (Pl. attach copy of valid STCC/ VAT clearance certificate)

1.3	Having achieved a minimum annual financial turn-over of Rs 5.00 crores in any one of the last five year exclusively in the business of solar PV alone.

(Pl. attach copy of audited balance sheet for 2008-09, 2009-10, 2010-11 and 2011-12 and 2012-13)

  - The firm must have designed, manufactured, tested supplied, erected, commissioned minimum capacity of 500KW (Cumulative over the period of last three years) in the range of 10 kW and above and which is/are in successful operation on the date of bid opening.

(Pl attach copies of PO’s and satisfactory report from previous installations in support of the same)

1.5	The firm must have set up at least one solar power plant of 50 KW or above capacity in the   premises of reputed  Government/Private  buildings  (or) Grid interactive solar power developers of 1 MW size or above with proven experience may also participate in tenders.

(Pl attach copies of PO’s and satisfactory report from previous installations in support of the same)

1.6	The firm must have adequate capacity to design , manufacture, test , supply, erect, and commission the power plant within the given time schedule.

(Pl furnish a brief write-up, backed with adequate data, explaining the available capacity and experience (both technical and commercial) for the manufacture and supply of the required systems and equipment within the specified time of completion after meeting all their current commitments.)

1.7	The products must conform to minimal technical requirements/ standards for off grid/standalone/grid connected solar PV power plants /systems to be deployed under the Jawaharlal Nehru National Solar Mission.

(Pl. attach copies of recent test certificates from SEC/ other authorized Test Centres of MNRE, GOI as proof thereof)

1.8	The  products/  systems/  devices  quoted  in  tender  should  be  as  per  MNRE specifications.

1.9	All above criteria should be strictly followed.	Tenderer should quote only if he is eligible.

- SCOPE OF SUPPLY & WORK:

2.0  BIDDER SCOPE OF WORK

2.1 Scope of Supply & Work includes all, design, engineering, manufacture, procurement & supply of equipment, and materials, testing at manufacturers works, inspection, packing and forwarding, supply, unloading at site, associated civil works, services, permits, installation and incidentals, insurance at all stages, erection, testing and commissioning of 100 kWp Grid Interactive Solar PV Power Plant with associated equipments and materials on turnkey basis at roof top of APSPDCL Complex with its Comprehensive Operation & Maintenance for 5 years thereafter.

2.2 The equipment and materials for 100kWp Grid Interactive Solar PV Power Plant with associated system (Typical) shall include but not be limited to the Supply, Erection, and Testing & Commissioning of the following:

- Solar PV modules in array including mounting frames, structures, foundation bolts and nuts for holding structures and module inter connection.

- Array Junction boxes, distribution boxes and fuse boxes. MCBs, Surge Arrestors

- Power Conditioning Units (PCU) with SCADA, & Weather Monitoring system to check Solar Irradiation, Wind Speed & Ambient Temperature.

- LT Power Interfacing Panel, Plant Monitoring Desk, D C Distribution board.

- Digital Voltage Meter and Ammeter, Kwh meters. Metering instrument and protection relays along with battery system.

- LT Power and Control Cables including end terminations and other required accessories for both AC & DC power.

- Data acquisition system.

- Lightning arrestors.

- PVC pipes and accessories/trenches.

- Tool kit and Earthing kit.

- Metering set and protection /Isolation systems,

- Earthing system for PV Array, DC power system, Lightning protection system

- Fire extinguishers , danger plates , name boards etc

- Transportation of equipments from Works to Site.

- Unloading, Loading of all supplied Equipments on Foundations at their respective places.

- Training of executive/technician.

- Control room equipments related to solar system etc

- Testing, maintenance and condition monitoring equipments.

- Mandatory spares for 5 years

- Any other equipment / material required to complete the 100 kWp Solar Power Plant on turnkey Basis. .

- Receipt, unloading, storage, erection, testing and commissioning of all supplied material.

2.3 Design of 100kWp Grid Interactive Solar Power Plant and its associated electrical & mechanical auxiliary systems includes preparation of single line diagrams and installation drawings, electrical lay outs, erection key diagrams, electrical and physical clearance diagrams, design calculations for Earth- mat, Bus Bar & Spacers etc design memorandum and other relevant drawings and documents required for engineering of all facilities are to be provided under this contract, are covered under Bidders scope of work.

2.4 In addition to above, the Bidder is required to measure the Solar Radiation and other climatic conditions. The major categories of site-specific assessment required are:

Global Solar Radiation (“GSR”)

Diffuse Solar Radiation (“DSR”)

Sunshine Duration

Temperature & Humidity

Wind Speed

2.5 Civil Works of shall be performed with respect to the following but not limited to:

o Design and construction of foundation for module mounting Structures having modules.

o Civil foundation work of for AC Distribution Board, DC distribution Board switchgears, etc

2. 6 Erection Work shall be performed with respect to the following but not limited to:

Solar PV Array.

Power Cables

Entire GI cable tray inside control room building

Fabrication, supply & erection of cable trays, support, brackets and accessories in case of site fabrication cable tray.

Galvanized steel rigid/flexible conduits and accessories, Hume pipes, ferrules, lugs,glands, terminal blocks, galvanized sheet steel junction boxes, cable fixing clamps, nuts and bolts etc. as required.

Supply of necessary steel materials for field fabrication of cable trays, supports, brackets, grounding system etc.

Stainless steel bolts & nuts, Washers (like Flat & Star) of suitable sizes only shall be used in interconnection PV module, arrays etc

2.7 Pre-commissioning & Commissioning of all supplied Equipments. Test running of Grid Connect Solar Power Plant as well as load trials at site, prior to handover and implementation of maintenance contract.

2.8 Any other items not specifically mentioned in the specification but which are required for erection, testing and commissioning and satisfactory operation of the solar power plant are deemed to be included in the scope of the specification unless specifically excluded on turnkey basis

2.9 Obtaining statutory approvals / clearances from Government Departments

2.10 The Bidder shall arrange deployment of manpower and required consumable during commissioning.

2.11 Power & Water as required for above Construction are to be arranged by the Bidder.

2.12 Total Operation & Maintenance of Solar Photovoltaic Power Plant for the 5 year‟s period including deployment of Engineering, Personnel. Technicians and etc.

2.13 All equipment & item which are not specifically mentioned but are required for completion of work including commissioning, operation & maintenance of Solar Photovoltaic Power Plant, in every respect and for safe and efficient operation and guaranteed performance without any extra cost .

2.14 Submission of following documents drawings data design and engineering information to APSPDCL or its authorized representative for review and approval in five copies.

(i) Detailed technical specification of all the equipments.

(ii) Design criteria.

(iii) Design calculations.

(iv) General arrangement an assembly drawings.

(v) Schematic diagram for entire electric system

(vi) G.A. drawings for, all types of structures, .

(VII) Quality assurance plans.

(viii) Test report (for type, acceptance, and routine tests).

(x) O&M Instruction s manuals and its drawings.

2.15 All drawings shall be fully corrected to agree with the actual "as built" site conditions and submitted to APSPDCL after commissioning of the project for record purpose.

2.16 The contractor shall forward to APSPDCL

(i) Schedule for various activities in the form of PERT Chart within a week from the date of detailed work order.

(ii)  Fortnightly site work progress report during construction period and

(iii) Monthly O&M reports after commissioning of the project.

2.17 Preparation and supply of detailed Operation, System and Maintenance manual of Power Plant.

2.18 Establishing a system to maintain an inventory of spare parts and tools, equipment, consumables and supplies for the facility’s and operation.

2.19 Employ and coordinate the training of personnel who will be qualified and experienced to operate and monitor the facility and to coordinate operations of the facility with the grid system.

2.20 Adequate insurance coverage during EPC.

2.21.1 One Solar Observatory including testing facilities shall be installed at site and operated by the contractor. During the O&M period, the Contractor shall keep the measured daily data at regular interval and provide the same to APSPDCL in electronic form. The right to use of the data shall remain with APSPDCL.

2.21.2 The grid supply connection would be provided with auto change over.

2.22 The  tenderer  shall  provide  the  necessary  training  to  identified  representative approved  by APSPDCL during the course of 5 years of CMC for proper daily operation and maintenance of installed system after being taken over by the  APSPDCL.

2.23 Training to the user for operation and maintenance of the system after 5 years.

2.24 Supply of manual for Operation and Maintenance of all the system in English.

2.25 Transmission and Distribution line upto ACDB.  It shall be the responsibility of the tenderer to provide distribution system.

2.26	Provide solar module with laminated plate inside the module showing name/ logo of manufacturer, model no. and serial no. along with RFID

2.27 SPV Power plant shall be installed as per the specifications provided in the technical offer.

2.28 Provide sealed & tested energy meter at consumption side & generation side of SPV Power Plant.

2.29 Civil work (grouting) for PV structure.

2.30 Fabrications, supply and the installation of suitable support for the PV panels and other components whichever is required with the accessories.

2.31 The subsidy component receivable from MNRE (30% of project cost) shall be obtained from MNRE itself the bidder being their channel partner for roof top/ Off grid solar projects

3.	INSTRUCTIONS TO BIDDERS

3.1 SUBSIDY FROM MNRE

3.1 100 kWp Ground Mounted Solar Power Project at APSPDCL Complex at Tirupati with its Comprehensive Operation & Maintenance for 5 years is being set up under the Programmee on “Off-grid and Decentralized Solar Applications”.

The subsidy component receivable from MNRE (30% of project cost) shall be obtained from MNRE itself the bidder being their channel partner for roof top/ Off grid solar projects.

3.2	Payment of cost of Tender documents: The collection of cost of Tender documents is dispensed away with, as there is no physical supply of tender documents and also to have absolute anonymity of bidder participating in e-procurement solution. The bidders can view/download the tender documents from the: www.eprocurement.gov.in.

3.3	Submission of bids:

i) Bids shall be submitted online on www.eprocurement.gov.in platform. The participating bidders in the tender should register themselves on  e-procurement platform in the website  www.eprocurement.gov.in.

ii) Bidders can log-in to e-procurement platform in Secure mode only by signing with the Digital certificates.

iii)  The bidders who are desirous of participating in e-procurement shall submit their technical bids, price bids as per the standard formats available at the e-market place.

- The bidders should scan and upload the copies of all the following documents in support of technical & price bids in proof of qualification requirement  duly signing on all the statements, documents & certificates uploaded by him, owning responsibility for their correctness/authenticity:

| S.No. | Description |
| --- | --- |
| Documents to be uploaded on-line as part of Technical bid proposal |  |
| 1 | Technical experience certificates issued by competent authority along with POs, agreements |
| 2 | Financial certificates for the last five years in proof of turn-over, Balance sheets, Profit & Loss A/c statements, Income Tax documents |
| 3 | Demand Draft towards Bid security from any schedule Bank |
| 4 | Annexures I to VII |
| 5 | Test certificates issued by MNRE/Approved MNRE test centres |
| 6 | Minimum guaranteed generation |
| 7 | Brief write-up, backed with adequate data, explaining the available capacity and experience (both technical and commercial) for the manufacture and supply of the required systems |
| 8 | Copy of EPF/Service Tax/STCC/ PAN/VAT clearance certificate. |
| 9 | Any other documents if required |

- For each uploaded document on line, the bidder should provide the index of the file names and its contents invariably

vi)   After uploading the documents, copies  of all the uploaded statements, certificates, documents   along with the original Demand Draft in respect of Bid Security  (except the Price bid / offer) are to be submitted by the bidder to the Chief General Manager / Projects/ APSPDCL, Tirupati so as to reach before the date and time of opening of the  technical bid. The Department shall not hold any risk on account of postal delay. Similarly, if any of the certificates, documents, etc., furnished by the bidder are found to be false/fabricated/ bogus, the bidder will be disqualified, blacklisted and action will be initiated as deemed fit and the Bid Security will be forfeited.

vii) The department will not hold any risk and responsibility regulating non-visibility of the      scanned and uploaded documents.

viii)   The Documents that are uploaded online on e-market place will only be considered for      Technical Bid Evaluation.

ix) Hard copies received after the deadline date & time, prescribed in document even though the bidder uploads the bid in the e-procurement platform will be summarily rejected treating them as late bids and/or returned unopened to the bidder.

- Important Notice to Contractors, Suppliers and  Department users:

- In the endeavor to bring total automation of processes in e-Procurement, the Govt. has issued orders vide G.O.Ms.No. 13 dated. 5.7.2006 permitting integration of electronic Payment Gateway of ICICI/HDFC Banks with e-Procurement platform, which provides a facility to participating suppliers/contractors to electronically pay the transaction fee online using their credit cards.

3.4	Price  Bid  Opening:  The  Price  Bids  will  be  opened  online  by  the  concerned officer/officers at the specified date & time and the result will be displayed on the: www.eprocurement.gov.in.  which can be seen by all the bidders who participated in the tenders.

3.5	Processing of Tenders: The concerned officer/officers will evaluate and process the tenders as done in the conventional tenders and will communicate the decision to the bidder online.

3.6	Validity period: The Tender shall remain valid for the period of ninety days from the date of opening of technical bid.

3.7	Tender without requisite amount of EMD shall be out rightly rejected.  No tenderer is exempted from EMD/ SD.  Correspondence on request from any tenderer on exemption of EMD / SD will not entertained by APSPDCL.

3.8	All the information furnished and document produced with the Tender shall be in English  language only.	The Tender notice and Tender document shall form a part of contract agreement.

3.9 The conditional tenders will be rejected out rightly.

3.10 APSPDCL reserves the right to reject/ accept any or all Tenders without assigning any reason thereof.

3.11 Period of completion of work is three months from the date of issue of work order.

3.12 Bidders must submit their bids for all items as stated above.

3.13 Bids must be submitted in English language only.

3.14 Prices quoted must be firm and fixed. No price variation / escalation shall be allowed.

3.15 Valid TIN / VAT/ Sales tax/Service Tax clearance certificate duly attested must be submitted along with the bid.

3.16 Deviations in terms and conditions, Specification of material, Inspection clause etc. will not be accepted under normal conditions.

3.17 Non/late  receipt  of  Original  EMD,  due  to  postal  delay  or  otherwise,  before  the scheduled date & time will not be considered and the bid shall be summarily rejected.

3.18  Since timely execution of works is of paramount importance, requests for extension of time shall not be ordinarily entertained.

3.19 Canvassing in any manner  shall not be entertained and will be viewed  seriously leading to rejection of the   bid.

3.20 Certificate to the effect that the systems to be supplied are indigenous & not fully imported must be furnished.

3.21 Copy of Test Reports from Solar Energy Centers (SEC)/Other Authorized Test Centres (OATC)  approved  by  MNRE,  GOI  in  regards  to  SPV  Systems  confirming  to  MNRE specifications or JNNSM norms and quoted standards under JNNSM.

3.22 Power of attorney to sign the agreement on behalf of bidders, if any, should be enclosed along with original bid documents.

3.23 Bids will be accepted & will be opened as per information mentioned in the notice- inviting tender. No receipt against submission of bid shall be issued by APSPDCL.

3.24 Bids  documents  along  with  original  EMD  should  be  submitted,  addressed to  the The Chief General Manager/Projects/APSPDCL/Tirupati. in a  sealed envelope super scribed “Bid for Solar PV systems against Bid Call Notice No. CGM/PROJECTS/APSPDCL/SIP-01/2013-14”.

3.25 The technical bid shall be opened online 27.05.2013 at 15.00 hrs

3.26 All pages of the bid documents must be signed & sealed by the authorized person on behalf of the bidders.

4.	PROCEDURE FOR OPENING THE BIDS

The procedure of opening of the bid shall be as under

4.1	TECHNICAL BID shall be opened online at the time & date mentioned in the bid notice by APSPDCL representative.

4.2	PRICE BID of only those bidders shall be opened who qualify in the technical evaluation. If necessary, the firms may be called for Technical Presentation of their product as per the time intimated by APSPDCL.

4.3	In case of supply of any defective material or substandard material, the materials will be rejected & it will be the responsibility of the supplier for taking back & replacing the rejected materials at their own cost. In case of non-lifting of such rejected materials within a reasonable time offered by the office it will have the right to suitably dispose off the same and forfeit the PBG amount.

4.4	The supplied materials should strictly comply with the specifications as mentioned in the bid; otherwise the material would be liable for rejection.

4.5	Any clarification on the technical specification and commercial terms and conditions may be clarified in writing from APSPDCL.

4.6	Deviation of any commercial terms and condition and technical specification shall not be entertained under any circumstances.

4.7	Bidders may in their own interest visit the sites and undertake site visit before submitting bids. APSPDCL will not be responsible for any incidental or consequential losses of the firms while execution and till expiry of the period of maintenance..

4.8	During the warranty period, MNRE/ State Agencies/ Users reserve the right to cross check  the  performance  of  the  systems  with  the  minimum  performance  levels specified in the MNRE specifications.

5.	EVALUATION OF OFFER

5.1. Eligibility Criteria:

The bidders will be short listed upon fulfilling the following techno commercial eligibility criteria.

5.1.1	Only MNRE approved organizations/ channel partners of ratings of 1A/ 1B/ PSU’s, who have got their products tested and qualified by any of the three authorized test centers and who have submitted information to the test centre about the company along with a copy to the Ministry in the MNRE format will be eligible to participate.

5.1.2	The firm must have valid EPF/Service Tax/STCC/ VAT clearance certificate.

5.1.3	Having achieved a minimum annual financial turn-over of Rs 5.00 crores in any one of the last five year exclusively in the business of solar PV alone.

    - The firm must have designed, manufactured, tested supplied, erected, commissioned minimum plant capacity of 500 KW (Cumulative over the period of last three years) in the range of 10 kW and above and which is/are in successful operation on the date of bid opening.

5.1.5 The firm must have set up at least one solar power plant of 50 KW or above capacity in the   premises of  reputed  Government/Private  buildings  (or) Grid interactive solar power developers of 1 MW size or above with proven experience may also participate in tenders.

5.1.6	The firm must have adequate capacity to design , manufacture, test , supply, erect, and commission the power plant within the given time schedule.

5.1.7	The products must conform to minimal technical requirements/ standards for off grid/standalone/Grid connected solar PV power plants /systems to be deployed under the Jawaharlal Nehru National Solar Mission.

5.1.8 The  products/  systems/  devices  quoted  in  tender  should  be  as  per  MNRE specifications.

6.0  Selection of Bidder:

The short listed bidders will be selected based on the price bid evaluation as given below.

6.1 The bids will be sorted in ascending order of the price quoted per Wp and the bidders will be selected with lowest price.

6.2	Financial bids shall be opened only for the technically eligible bidders. The bidders would be short listed based on the lower cost offered.

6.3	If project cost proposed in the bid is more than the reserved price (Rs.103/Wp) the bids will get cancelled.

6.4	In case sufficient no. of bids are not received, the APSPDCL reserves the right to reallocate / revise the allocation/ cancel / postpone the tender.

6.5	The right of allotment of works to the contractors is reserved with the APSPDCL.

6.6	EMPLOYER’S RIGHT to Vary Quantities at the time of Award

The Employer reserves the right at the time of contract award to increase or decrease the quantity of work specified in the Schedule without any change in unit price or other terms and conditions.

The Employer reserves the right to vary the ordered quantity upto 50% during the execution of the contract.

7.	 NOTIFICATION OF AWARD AND SIGNING OF AGREEMENT

7.1	The Bidder whose Bid has been accepted will be notified of the award by the Employer prior to expiration of the Bid period by cable, telex or facsimile confirmed by registered letter. This letter (hereinafter in the Conditions of Contract called the “Letter of Acceptance”) will state the sum that the Employer will pay the Contractor in consideration of the execution, completion, and maintenance of the works by the contractor as prescribed by the Contract (hereinafter and in the Contract called the ”Contract Price”).

7.2	The notification of award will constitute the formation of the Contract, subject only to the furnishing of a performance security in accordance with the provisions of Clause 32 and signing of agreement.

7.3	The contract agreement will incorporate all agreements between the Employer and the successful Bidder.

7.4	Upon the furnishing by the successful Bidder of the performance Security, the Employer will promptly notify the other Bidders that their Bids have been unsuccessful.

7.5	The bidder shall produce TIN (Tax Payer Identification Number) before issue of Letter of Acceptance.

8.	 PERFORMANCE SECURITY

8.1	Within fifteen (15) days of receipt of the Letter of Acceptance, the Successful Bidder shall deliver to the Employer a Performance Security in any of the forms given below for an amount equivalent to 10 % of the Contract price.

- one No. bank guarantee for an amount equivalent to 10% of total agreement value for the work of Design, supply, erection and commissioning of 100KWp solar plant on roof top of corporate office, APSPDCL, Tirupati with associated equipments i.e., valid for Five years three months from the date of entering the agreement in the form given Annexure-A.

(or)

- 1No. Bank draft with above value, in favour of Accounts Officer/ CPR/APSPDCL/Tirupati, payable at Tirupati drawn on any Nationalized Bank.

8.2	If the performance security is provided by the successful Bidder in the form of a Bank Guarantee, it shall be issued by a Nationalized Bank and shall be acceptable to the Employer.

8.3	Failure of the successful Bidder to comply with the requirements of Sub-Clause 32.1 shall constitute sufficient grounds for cancellation of the award and forfeiture of the Bids Security.

9.	PAYMENT TOWARDS PRICE ADJUSTMENT:

The rates and prices quoted by the bidder shall be firm throughout the contract period. Price adjustment/variation is not allowed.

10	MODE OF PAYMENT:

10.1	All payments shall be made promptly by the Employer on or after thirty (30) days of receipt of contractor’s invoice complete in all respects and supported by the requisite documents and fulfillment of stipulated conditions, if any. All the payment shall be released to the contractor directly.

10.2	All invoices under the contract shall be raised by the contractor on APSPDCL and all payments shall be made to the contractor by Chief General Manager/ Finance on behalf of APSPDCL.

11. CORRUPT OR FRAUDULENT PRACTICES.

11.1 APSPDCL Bidders/ Contractors/ Contractors observe the highest standard of ethics during the procurement and execution of such contracts.  In pursuance of this policy, APSPDCL:

- Defines, for the purposes of this provision, the terms set forth below as follows:

- “Corrupt Practice” means the offering, giving, receiving or soliciting of any thing of value to influence the action of a public official in the procurement process or in contract execution, and

- “Fraudulent Practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the detriment of the Borrower, and includes collusive practice among Bidders (prior to or after bid submission) designed to establish bid prices at artificial non-competitive levels and to deprive the Borrower of the benefits of free and open competition.

- Will reject a proposal for award if it determines that the Bidder recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question.

- Will declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a Bank financed contract if it at any time determines that the firm has engaged in corrupt or fraudulent practices in competing for, or in executing a Bank-financed contract.

11.2 Furthermore, Bidders shall be aware of the provision stated in sub-clause 23.2 .

12.	QUALITY ASSURANCE PLAN:

The quality assurance plan of contractor shall be generally in accordance with bid conditions. This information shall be furnished with his bids as per G&T of clause 72, failing which his bid shall be liable for rejection.

GENERAL TERMS & CONDITIONS

1.1	Rate:

The offer should indicate the unit cost of the system, Design, Testing Installation & Commissioning charges, O&M Charges and taxes & duties separately. The unit cost must be inclusive of packing, forwarding, loading & unloading  charges,  cost  of  insurance  and  transportation  FOR destination where the system will be installed as per the work order.

1.2	Sales Tax & Duties etc.:

All Taxes and duties as prescribed both under Central and State Government sales tax rules would be applicable.

1.3	Earnest Money Deposit:

1.3.1	Earnest money deposit as specified in Tender Notice is required to be deposited along with the bid without which the bid will not be accepted. No interest will be payable for the EMD amount under any circumstances.

1.3.2	Earnest money can be deposited in shape of a Demand Draft in favour of AO/CPR/APSPDCL/Tirupati from any Nationalised Bank Payable at Tirupati and the proof of deposits should be attached to the bid.

1.3.3	E.M.D would be refunded to the unsuccessful Bidders after finalization of the bid without any interest.

1.3.4	E. M. D would be forfeited in case of non- compliance of the purchase order T/C by the successful bidder.

1.4 Programme Execution Schedule :

6.5.1	Delivery of systems at sites: 1 month from the date of handing over the site

to the vendor for the purpose of erection of the PV power plant.

    - Installation & Commissioning:2 months from the date of preliminary and

    - performance guarantee inspection, physical verification. and test handing over of systems

for installation.

The above dates are not extended under any circumstances.

1.4.1	Upon intimation about commissioning of the systems by the executing firm a joint inspection will be carried out by the representatives of the executing firm, APSPDCL.

1.5	Validity of offer:

The offer must be kept valid for a period of 90 days from the date of opening of the technical bid. No escalation clause except the admissible tax component under the period of consideration would be accepted. The validity can be further extended with mutual consent as per merit of the case.

1.6 Warranty:

The complete system should be warranted against any manufacturing defect or  bad workmanship at least for a period of 5 (five) years from the date of commissioning of the systems.

The offered module shall have a power warranty of 25 years against any manufacturing defect of bad workmanship with degradation of power generated not exceeding 15% of the minimum rated power over the 25 year period and not more than 10% after ten years period. All warranties from the manufacturer have to be fully endorsed by the bidder.

After one year of installation of SPV plant, 10% of the installed modules will be selected randomly and will be tested in the Laboratory in the  APSPDCL or test centre approved by MNRE for STC performance, if 50% or more of the modules are found below the rated STC power rating then the buyer will test all the panels and the bidder will be required to replace all the underperforming modules with new modules.

Warranty certificate to the above effect must be furnished along with the commissioning reports.

Any defect noticed during warranty period should be rectified/replaced by the supplier free of cost upon due intimation by APSPDCL. The supplier fails to replace the module/Inverters within 15 days from the date of defect noticed, SPDCL will replace the defective and same amount will be deducted from the supplier CMC yearly bill.

1.7  GUARANTEED GENERATION:

The tenderer shall give a guaranteed generation of minimum 4 units (kWh) per kW per day from SPV Power Plant during 300 sunny days in a year during comprehensive maintenance contract  period. Otherwise, tenderer have  to  pay  an  amount  of  Rs.50/- per  unit  as compensation for the number of units not supplied against the guaranteed generation.  The tenderer shall provide  sealed & tested energy meter at consumption side of SPV Power Plant. Tenderer should  quote the guaranteed generation in the offer. Daily reports of installed system duly certified by concerned authorised APSPDCL Engineer will be submitted by the tenderer to APSPDCL.

2 IDENTIFICATION AND TRACEABILITY

2.1 Each PV module used in any solar power project must use a RF identification tag (RFID), which must contain the following information. The RFID can be inside or outside the module laminate, but must be able to withstand harsh environmental conditions.

(i) Name of the manufacturer of PV Module

(ii) Name of the Manufacturer of Solar cells

(iii) Month and year of the manufacture (separately for solar cells and module)

(iv) Country of origin (separately for solar cells and module)

(v) I-V curve for the module

(vi) Peak Wattage, Im, Vm and FF for the module

(vii) Unique Serial No and Model No of the module

(viii) Date and year of obtaining IEC PV module qualification certificate

(ix) Name of the test lab issuing IEC certificate

(x) Other relevant information on traceability of solar cells and module as per

ISO 9000 series.

3	Penalty and termination of contract:

The systems shall be supplied, installed and commissioned within the scheduled time. If the supplier fails to adhere to the schedule, APSPDCL shall without prejudice to its other remedies under the contract deduct from the contract price as liquidated damages a sum equivalent to 0.5% of the delivery price of the delayed goods or unperformed services for each week of delay until actual delivery or installation/commissioning up to a maximum deduction of 10% of  the  contract  price  for  delayed  goods  or  installation  and  commissioning.  Once the maximum is reached (i.e. 14 weeks of delay) APSPDCL may consider termination of the contract and forfeit the security deposit without prejudice to the other remedies of the contract.

However, Competent Authority, APSPDCL, may at his own discretion allow reasonable time extension upon written application of the supplying firm. If the delay is considered intentional or due to negligence of the vendor extension can be allowed with imposition of penalty. If the delay is considered to be genuine time extension can be allowed without imposition of penalty.

4	Force Majeure:

The supplier of the SPV system shall not be charged with liquidated damages nor shall his security for performance be forfeited when failure of the supplier in making delivery is due to any event beyond the control of the supplier and could not have been foreseen, prevented or avoided by a prudent person. These include, but are not restricted to acts of God, acts of public enemy, acts of Government, fires, floods, epidemics, strikes, freights, embargoes and unusually severe weather.

5	Inspection:

5.1	Pre delivery inspection of solar PV modules and other major components will be carried out by a team of designated officials of APSPDCLas may be considered appropriate at the factory site of the vendor.

5.2 APSPDCL has the right to have the tests carried out at bidder’s cost by an independent agency at any point of time.

Tenderer shall inform APSPDCL in writing when any portion of the work is ready for inspection giving sufficient notice to enable APSPDCL to send representative to inspect the same without  affecting the further progress of the work. The work shall not be considered in accordance with the terms of the contract until the competent person from APSPDCL certifies in writing to that effect.

Approval of material or workmanship or approval of part of the work during the progress of execution shall not bind the APSPDCL or in any way affect him even to reject the work which is alleged to be completed and to suspend the issue of his certificate of completion until such alteration and modifications or reconstruction have been effected at your cost as shall enable him to certify that the work has been completed to his satisfaction.

6	Payment:

Payment will be released as follows:

6.1	25% of the cost of material supplied will be released on raising the bills towards cost of supplies only.  The payment will be released @25% on each occasion in three tranches i.e. (i) on receiving panels with accessories (ii) PCU and (iii) others.

6.2	85% of the tendered cost minus payments released against item No.1 above, will be released after supply, installation & successful commissioning of the systems duly certified by Tenderer, and APSPDCL.

6.3	15% of the tendered cost shall be released on submission of one month successful performance report of the system duly certified by APSPDCL and submission of performance bank guarantee of 10% of total project cost from any Nationalized Bank valid for period of 5 years and two months.

6.4	Comprehensive Maintenance Contract (5 Years from date of completion of plant)

  - Payment will be made after successful completion of 1 year duly deducting penalties and other recoveries if necessary

  - Payments will be made yearly upto completion of CMC

7	Execution:

Execution of work shall be carried out in an approved manner as outlined in the technical specification or where not outlined, in accordance with relevant Indian Standard Specification, to the reasonable satisfaction of the Authorized APSPDCL Officer.

8	Limitation of Liability:

APSPDCL, will, in no case be responsible for any accident fatal or non-fatal, caused to any worker or outsider in course of transport or execution of work.  All the expenditure including treatment or compensation will be entirely borne by the Executants. The Executants shall also be responsible for any claims of the workers including PF, Gratuity, ESI & other legal obligations

9.  LANGUAGE AND LAW

9.1	The language of the Contract is English and the law governing the Contract are stated in the Contract Data.

10.	ENGINEERS DECISIONS

10.1	Except where otherwise specifically stated, the Engineer will decide contractual matters between the Employer and the Contractor in the role representing the Employer.

11.   DELEGATION

11.1	The Engineer, named in the Contract Data, or any other competent person appointed by the Employer and notified to the Contractor, to act in replacement of the Engineer, is designated by the Employer to represent the Employer in all dealings with the Contractor concerning the work, including administering the Contract, certifying payments due to the Contractor, issuing and valuing Variations to the Contract, awarding extensions of time, and valuing the Compensation Events.

11.2	The Engineer may delegate any of his duties and responsibilities to other people except to the Adjudicator after notifying the Contractor and may cancel any delegation after notifying the contractor

11.3	The Contractor shall designate in writing to the Employer, a representative, to be its representative in all dealings with the Employer concerning the Works.

12	COMMUNICATIONS

12.1	Communications between parties which are referred to in the conditions are effective only when in writing. A notice shall be effective only when it is delivered (in terms of Indian Contract Act).

13.	SUBCONTRACTING

13.1	Subcontracting is not allowed.

  - Site measurements

Site measurements of Corporate office building at APSPDCL, Tirupati for SPV Plant

1) 3 rd floor Main building dimensions 	: 128X34= 4350 sqft

2) LMC% Traninig Centre			: 193X16= 3088 Sqft

3) IT wing block				: 119X16= 1904 Sqft

Total					:	     9342 Sqft

15.	PERSONNEL

15.1	The Contractor shall employ the key personnel named in the Schedule of Key Personnel as referred to in the Contract Data to carry out the functions stated in the Schedule to other personnel approved by the Engineer.  The Engineer will approve any purposed replacement of Key personnel only if their qualifications, abilities, and relevant experience are substantially equal to or better than those of the personnel listed in the Schedule.

15.2	If the Engineer asks the Contractor to remove a person who is a member of the Contractor’s staff or his work force stating the reasons the Contractor shall ensure that the person leaves the site within seven days and has no further connection with the work in the Contract.

16.	 EMPLOYER’S AND CONTRACTORS RISKS

16.1	All risks of loss of or damage to physical property and of personal injury and death which arise during and in consequence of the performance of the Contract other than the excepted risks are the responsibility of the Contractor.

17.	INSURANCE

17.1	The following insurance cover is to be provided by the Contractor in the joint names of the Employer and the contractor for the period from the Start Date to the end of the Defects Notice Period or of the last Defects Correction Period whichever is the later.

- Full cover against damage to other people’s properly caused by the Contractor’s acts or omissions;

- Cover against death or injury caused by the Contractor’s acts or omission to

any one authorized to be on the site.

c)	third parties who are not on the site; as per laws applicable in India.

d)		Full cover against damage to the Works, materials and equipments during storage and construction.

Contractor shall pursue the matters related to insurance claims in association with the Employer.

17.2	Policies and certificates for insurance are to be produced by the Contractor to the Employer for approval before the Start Date given in the Contract Data and subsequently as the Employer may require. All such insurance shall provide for compensation to be payable in the types and proportions of currencies required to rectify the loss or damage incurred.

17.3	If the Contractor does not provide any of the policies and certificates required, the Employer may effect the insurance which the Contractor should have provided and recover the premiums the Employer has paid from payments otherwise due to the Contractor or, if no payment is due, the payment of the premiums shall be a debt due.

17.4	Alterations to the terms of insurance may be made either with the approval of the employer or as a result of general change imposed by the insurance company with which the Insurance policy is effected.

17.5	Both parties shall comply with any conditions of the insurance policies.

17.6	Insurance coverage for all items shall be at the risk of the contractor.

18.	  SITE INVESTIGATION REPORTS

18.1	The Contractor, in preparing the Bid, shall rely on any site Investigation Reports referred to in the Contract Data, supplemented by any information available to the Bidder.

19.	QURIES ABOUT THE CONTRACT DATA

19.1	The Engineer will clarify queries on the Contract Data.

20.	CONTRACTOR TO CONSTRUCT THE WORKS

20.1	The Contractor is responsible for design, shop test, and arranging for inspection of tests by representatives nominated by the employer, supply, transport, construct, install, testing and commissioning and hand over the Works in accordance with the relevant Specifications and Drawings.

21.	THE WORKS TO BE COMPLETED BY THE INTENDED COMPLETION DATE

21.1	The Contractor may commence execution of the Works on the Start Date and shall carry out the Works in accordance with the program submitted by the Contractor as updated with the approval of the Engineer, and complete them by the intended completion Date.

22.	APPROVAL BY THE ENGINEER

22.1	The Contractor shall submit Specifications and Drawings showing the proposed Temporary Works to the Engineer, who is to approve them if they comply with the Specifications and Drawings.

22.2	The Contractor shall be responsible for design of Temporary Works.

22.3	The Engineer’s approval shall not alter the Contractor’s responsibility for design of the Temporary Works.

22.4	All Drawings prepared by the Contractor for the execution of the temporary or permanent Works are subject to prior approval by the Engineer before their use.

25.	SAFETY

25.1	The Contractor shall be responsible for the safety of all activities on the Site.

26.	DISCOVERIES

26.1	Anything of historical or other interest or of significant value unexpectedly discovered on the Site is the property of the Employer. The Contractor is to notify the Engineer of such discoveries and carry out the Engineer’s instructions for dealing with them.

27.	POSSESSION OF THE SITE

27.1	The Employer shall give possession of all parts of the Site to the Contractor. If possession of the part is not given by the date stated in the Contract Data the Employer is deemed to have delayed the start of the relevant activities and this will be Compensation Event.

28.	 ACCESS TO THE SITE

28.1	The Contractor shall allow the Engineer and any person authorized by the Engineer access to the Site, to any place where work in connection with the Contract is being carried out or is intended to be carried out and to any place where materials or plant are being manufactured/fabricated/assembled for the works.

29.	 INSTRUCTIONS

29.1	The Contractor shall carry out all instructions of the Engineer which comply with the applicable laws where the Site is located.

29.2	The Contractor shall permit the bank to inspect the Contractor’s accounts and records relating to the performance of the Contractor and to have them audited by auditors appointed by the Bank, if so required by the Bank.

30.	CONTRACTOR’S MATERIALS BROUGHT ON TO SITE

30.1	The Contractor shall bring to Site all equipment, components, parts, materials, including construction equipment, tools and tackles for the purpose of the works under intimation to the Engineer.  All such goods shall, from the time of their being brought vest in the Employer, but may be used for the purpose of the works only and shall not on any account be removed or taken away by the Contractor without the written permission of the Engineer.  The Contractor shall nevertheless be solely liable and responsible for any loss or destruction thereof and damage thereto.

30.2	The Employer shall have a lien on such goods for any sum or sums which may at any time be due or owing to him by the Contractor, under, in respect of or by reasons of the Contract.  After giving a fifteen (15) days notice in writing of his intention to do so, the Employer shall be at liberty to sell and dispose off any such goods, in such manner as he shall think fit including public auction or private treaty and to apply the proceeds in or towards the satisfaction of such sum or sums due as aforesaid.

30.3	After the completion of the Works, the Contractor shall remove from the Site under the direction of the Engineer the materials such as construction equipment, erection tools and tackles, scaffolding etc. with the written permission of the Engineer.  If the Contractor fails to remove such materials, within fifteen (15) days of issue of a notice by the Engineer to do so then the Engineer shall have the liberty to dispose off such materials as detailed under Clause 29.2 above and credit the proceeds thereto to the account of the Contractor.

31.	PROTECTION OF PROPERTY AND CONTRACTOR’S LIABILITY

31.1	The Contractor shall be responsible for any damage resulting from his operations.  He shall also be responsible for protection of all persons including members of public and employees of the Employer and the employees of other Contractors and Sub-Contractors and all public and private property including structures, building, other plants and equipment and utility either above or below the ground.

31.2	The Contractor will ensure provision of necessary safety equipment such as barriers, signboards, warning lights and alarms, etc. to provide adequate protections to persons and property.  The Contractor shall be responsible to give reasonable notice to the Engineer and the Employer of public or private property and utilities when such property and utilities are likely to get damaged or injured during the performance of his works and shall make all necessary arrangements with such Employers, related to removal and/ or replacement or protection of such property and utilities.

- PAINTING

All exposed metal parts of the equipment including piping, structures, railing etc. wherever applicable, after installation unless otherwise surface protected, shall be first painted with at least one coat of suitable primer which matches the shop primer paint used, after thoroughly cleaning all such parts of all dirt, rust, scales, grease, oil and other foreign materials by wire brushing, scraping or sand blasting and the same being inspected and approved by the Engineer for painting. Afterwards, the above parts shall be finished painted with two coats of allowed resin machinery enamel paints. The quality of the finish paint shall be as per the standards of ISI or equivalent and shall be of the colour as approved by the Engineer.

33.	TRANSPORT ARRANGEMENT

The contractor shall make the transport arrangement at his cost for his staff and workers to site.

34.	INCOME TAX

  - Deductions will be made towards Income Tax at source by the APSPDCL as directed by Income Tax Department.

b)	The Contractor’s staff, personnel and labour will be liable to pay personnel income taxes in India in respect of such of their salaries and wages as are chargeable under the laws and regulations for the time being in force, and the contractor shall perform such duties in regard to such deductions there of as may be imposed on him by such laws and regulations.

35.	TERMINATION OF CONTRACT FOR APSPDCL CONVENIENCE

The APSPDCL shall be entitled to terminate this contract at any time for the APSPDCL convenience after giving 30 days prior notice to the contractor with a copy to the Engineer.

36.	ARBITRATION

The Procedure for arbitration will be as laid down Indian Arbitration and conciliation act 1996.

37.	INSPECTION, TESTING AND INSPECTION CERTIFICATES

The provisions of the clause entitled Inspection, Testing and Inspection Certificates under Technical Specifications, Section shall also be applicable to the erection portion of the Works. The Engineer shall have the right to re-inspect any equipment though previously inspected and approved by him at the Contractor’s works, before and after the same are erected at Site. If by the above inspection, the Engineer rejects any equipment, the Contractor shall make good for such rejections either by replacement or modifications/repairs as may be necessary to the satisfaction of the Engineer. Such replacement will also include the replacements or re-execution of such of those works of other Contactors and/or agencies, which might have got damaged or affected by the replacements or re-work done to the Contractor’s work.

The above inspection will be done by the departmental officers or any third party opted by APSPDCL. All the materials shall comply with IS/IE standards as specified in Technical specifications in the bid.

38.	ACCESS TO SITE AND WORKS ON SITE

## 38.1	Suitable access to and possession of the Site shall be afforded to the Contractor by the Employer in reasonable time.

## 38.2	The works so far as it is carried out on the Employer’s premises, shall be carried out at such time as the Employer may approve and the Employer shall give the Contractor reasonable facilities for carrying out the works.

## 38.3	In the execution of the works, no person other than the Contractor or his duly appointed representative, Sub- Contractor and workmen, shall be allowed to do work on the Site, except by the special permission, in writing of the Engineer or his representative.

39.	CONTRACTOR’S SITE OFFICE ESTABLISHMENT

The Contractor shall establish a Site Office at the site and keep posted an authorized representative for the purpose of the Contract. Any written order or instruction of the Engineer or his duly authorised representative shall be communicated to the said authorised resident representative of the Contractor and the same shall be deemed to have been communicated to the Contractor at his legal address.

40.	DISCIPLINE OF WORKMEN

The Contractor shall adhere to the disciplinary procedure set by the Engineer in respect of his employees and workmen at Site.  The Engineer shall be at liberty to object to the presence of any representative or employee of the Contractor at the Site, if in the opinion of the Engineer such employee has misconducted himself or is incompetent or negligent or otherwise undesirable and then the Contractor shall remove such a person objected to and provide in his place a competent replacement.

41.	CONTRACTOR’S FIELD OPERATION

## 41.1	The Contractor shall keep the Engineer informed in advance regarding his field activity plans and schedules for carrying-out each part of the works.  Any review of such plan or schedule or method of work by the Engineer shall not relieve the Contractor of any of his responsibilities towards the field activities.  Such reviews shall also not be considered as an assumption of any risk or liability by the Engineer or the Employer or any of his representatives and no claim of the Contractor will be entertained because of the failure or inefficiency of any such plan or schedule or method of work reviewed. The Contractor shall be solely responsible for the safety, adequacy and efficiency of plant and equipment and his erection methods.

## 42.2	The Contractor shall have the complete responsibility for the conditions of the Work-site including the safety of all persons employed by him or his Sub–Contractor and all the properties under his custody during the performance of the work. This requirement shall apply continuously till the completion of the Contract and shall not be limited to normal working hours.  The construction review by the Engineer is not intended to include review of Contractor’s safety measures in, on or near the Work-Site, and their adequacy or otherwise.

43.	SAFETY PRECAUTIONS

## 43.1	All the safety measures to avoid accidents shall be following strictly in accordance with the safety rules and regulations laid down by the Government authorities. The Contractor shall take all safety precautions and shall provide proper scaffolding, lifebelts, ladder shock proof helmets, etc. to avoid accidents and to ensure safety, of not only his personnel but also the safety of the staff and workers of other contractors working at the same site.

## 43.2	The contractor shall take necessary precautions to ensure that no part of the building/structure damage or disfigures due to negligence on his part while carrying out the work.   In case of excess damage, the same shall be made good by the contractor immediately at his own cost.  Recommissioning on energized equipment shall be carried out with proper safety permits issued by the Purchase/Competent authorities.  When required to work at heights or at hazardous location areas, the contractor shall carry out the same with utmost care and all safety precautions.

44.	FIRE PRECAUTIONS

The contractor shall strictly instruct his site staff and workers to abide by the regulations in the force at the site regarding all precautions to be taken to avoid the hazards.

45.	PHOTOGRAPHS AND PROGRESS REPORT

## 45.1	The Contractor shall furnish three (3) prints each to the Engineer of progress photographs of the work done at Site. Photographs shall be taken as and when indicated by the Engineer or his representative. Photographs shall be adequate in size and number to indicate various stages of erection.  Each photograph shall contain the date, the name of the Contractor and the title of the photograph.

## 45.2	The above photographs shall accompany the monthly progress report detailing-out the progress achieved on all erection activities as compared to the schedules.  The report shall also indicate the reasons for the variance between the scheduled and actual progress and the action proposed for corrective measures, wherever necessary.

46.	MAN-POWER REPORT

## 46.1	The Contractor shall submit to the Engineer, on the first day of every month, a skilled/unskilled man hours schedule for the month, detailing the man hours scheduled for the month, skill-wise and area-wise.

## 46.2	The Contractor shall also submit to the Engineer, on the first day of every month, a man-power report of the previous month detailing the number of persons scheduled to have been employed and actually employed, skill-wise and the areas of employment of such labour.

47.	PROTECTION OF WORK

The Contractor shall have total responsibility for protecting his works till it is finally taken over by the Engineer.  No claim will be entertained by the Employer or by the Engineer for any damage or loss to the Contractor’s works and the Contractor shall be responsible for complete restoration of the damaged works to original conditions to comply with the specification and drawings, should any such damage to the Contractor’s works occur because of any other party not being under his supervision or control.  The Contractor shall make his claim directly with the party concerned.  If disagreement or conflict or dispute develops between the Contractor and the other party or parties concerned regarding the responsibility for damage to the Contractor’s works, the same shall be resolved as per the provisions of the Clause 7.0 above entitled “Cooperation with other Contractors”.  The Contractor shall not cause any delay in the repair of such damaged works because of any delay in the resolution of such dispute.  The Contractor shall proceed to repair the Work immediately and no cause thereof will be assigned pending resolution of such disputes.

48.	EMPLOYMENT OF LABOUR

## 48.1	The Contractor will be expected to employ on the work only his regular skilled employees with experience of his particular work.  No female labour shall be employed after darkness.  No person below the age of eighteen years shall be employed.

## 48.2	All traveling expenses including provisions of all necessary transport to and from Site, lodging allowances and other payments to the Contractor’s employees shall be the sole responsibility of the Contractor.

## 48.3	The hours of work on the Site shall be decided by the Employer and the   Contractor shall adhere to it.  However, working hours will normally be eight (8) hours per day -Monday through Saturday.

48.4	In case the Employer becomes liable to pay any wages or dues to Labour or any Government agency under any of the provisions of the Minimum Wages Act, Workmen Compensation Act, Contract Labour Regulation Abolition Act or any other law due to act of omission of the Contractor, the Employer may make such payment and shall recover the same from the Contractor’s bills.

49.	COMPLIANCE WITH LABOUR REGULATIONS

49.1	During continuance of the contract, the Contractor and his sub-contractors shall abide at all times by all applicable existing labour enactments and rules made there-under, regulations, notifications and byelaws of the State or Central Government or local authority and any other labour law (including rules), regulations, bye laws that may be passed or notification that may be issued under any labour law in future either by the State or the Central Government or the local authority.  The employees of the Contractor and the Sub-contractor in no case shall be treated as the employees of the Employer at any point of time.

49.2	The Contractor shall keep the Employer indemnified in case any action is taken against the Employer by the competent authority on account of contravention of any of the provisions of any Act or rules made there under, regulations, or notifications including amendments.

49.3	If the Employer is caused to pay under any law as Principal Employer such amount as may be necessary to cause or observe, or for non-observance of the provisions stipulated in the Notifications/Byelaws/Acts/Rules/Regulations including amendments, if any, on the part of the Contractor, the Employer shall have the right to deduct any money due to the Contractor under this contract or any other contract with the Employer including his amount of performance security for adjusting the aforesaid payment.  The Employer shall also have right to recover from the Contractor any sum required or estimated to be required for making good the loss or damage suffered by the Employer.

49.4	Salient features of some major laws applicable to establishments engaged in   building and other construction works:

- Workmen Compensation Act 1923: The Act provides for compensation in case of injury by accident arising out of and during the course of employment.

- Payment of Gratuity Act 1972: Gratuity is payable to an employee under the Act on satisfaction of certain conditions on separation if an employee has completed 5 years service or more or on death the rate of 15 days wages for every completed year of service.  The Act is applicable to all establishments employing 10 or more employees.

    - Employee P.F. and Miscellaneous Provision Act 1952: The Act provides for more contribution by the Employer plus workers @ 10% or 8.33%.  The benefits under these are :

    - Pension or family pension on retirement or death, as the case may be.

    - Deposit linked insurance on death in harness of the worker.

    - Payment of P.F. accumulation on retirement/death etc.

- Maternity Benefit Act 1951: The Act provides for leave and some other benefit for women employees in case of confinement or miscarriage etc.

- Contract Labour (Regulation & Abolition) Act 1970: The Act provides for certain welfare measures to be provided by the Contractor to contract labour and in case contractor fails to provide, the same are required to be provided, by the Principal Employer by law. The Principal Employer is required to take Certification of Registration and the Contractor is required to take license from the designated Officer.  The Act applicable to the establishments or contractor of Principal Employer if they employ 20 or more contract labour.

- Minimum Wages Act 1948: The Employer is supposed to pay not less than the Minimum Wages fixed by appropriate Govt. as per provision of the Act if the employment is scheduled employment.

- Payment of Wages Act 1936:  It lays down as to by what date the wages are to be paid, when it will be paid and what deductions can be made from the wages of the workers.

- Equal Remuneration Act 1979:  The Act provides for payment of equal wages for work of equal nature to male and female workers and for not making discrimination against female employees in the matters of transfer, training and promotions etc.

- Payment of Bonus Act 1965: The Act is applicable to all establishments employing 20 or more employees. The Act provides for payments of annual bonus subject to a minimum of 8.33% of wages and maximum of 20% of wages to employees drawing Rs. 3500/- per month or less.  The bonus is to be paid to employees getting Rs. 2500 per month or above upto Rs. 3500/- per month shall be worked out by taking wages of Rs. 2500/- per month only.  The Act does not apply to certain establishments. The newly set-up establishments are exempted for five years in certain circumstances. Some of the State Governments have reduced the employment size from 20 to 10 for the purpose of applicability of this Act.

- Industrial Dispute Act 1947: The act lays down the machinery and procedure for resolution of industrial disputes, in what situations as strike or lock-out becomes illegal and what are the requirements for laying off or retrenching the employees or closing down the establishment.

- Industrial Employment (Standing Orders) act 1946: It is applicable to all establishments employing 100 or more workmen (employment size reduced by some of the States and Central Government to 50). The Act provides for laying down rules governing the conditions of employment by the Employer on matters provided in the Act and get the same certified by the designated Authority.

- Trade Unions Act 1926: The Act lays down the procedure for registration of trade; unions of workmen and Employers.  The Trade; Unions registered under the Act have been given certain immunities from civil and criminal liabilities.

- Child Labour (Prohibition & Regulation) Act 1986: The Act prohibits employment of children below 14 years of age in certain occupations and processes and provides for regulations of employment of children in all other occupations and processes.  Employment of Child Labour is prohibited in building and Construction Industry.

- Inter-State Migrant Workmen’s (Regulation of Employment & Conditions of Service) Act 1979:  The Act is applicable to an establishment which employs 5 or more inter-state migrant workmen through an intermediary (who has recruited workmen in one state for employment in the establishment situated in another state). The Inter-State migrant workmen, in an establishment to which this Act becomes applicable, are required to be provided certain facilities such as; housing, medical aid, traveling expenses from home upto the establishment and back, etc.

- The Building and Other Construction Workers (Regulation of Employment and Conditions of Service) Act 1996 and the Cess Act of 1996: All the establishments who carry on any building or other construction work and employ 10 or more workers are covered under this Act. All such establishments are required to pay cess at the rate not exceeding 2% of the cost of construction as may be modified by the Government. The Employer of the establishment is required to provide safety measures at the building or construction work and other welfare measures, such as canteens, first-aid facilities, ambulance, housing accommodations for workers near the work place etc.  The Employer to whom the Act applies has to obtain a registration certificate from the Registering Officer appointed by the Government.

- Factories Act 1948: The Act lays down the procedure for approval at plans before setting ;up a factory, health and safety provisions, welfare provisions, working hours, annual earned leave and rendering information regarding accidents or dangerous occurrences to designated authorities.  It is applicable to premises employing 10 persons or more with aid of power or 20 or more persons without the aid of power engaged in manufacturing process.

50.	FACILITIES TO BE PROVIDED BY THE EMPLOYER

50.1	Space

Land for Contractor’s Office, Store, Workshop etc.

a)	The Engineer shall at his discretion and for the duration of execution of the Contract make available at site, land for construction of Contractor’s field office, workshop, stores, magazines for explosives in isolated locations, assembling yard, etc. required for execution of the Contract. Any construction of temporary roads, offices, workshop, etc. as per plan approved by the Engineer shall be done by the Contractor at his cost.

b) 	On completion of work the Contractor shall hand over the land duly cleaned to the Engineer. Until and unless the Contractor has handed over the vacant possession of land allotted to him for the above purpose, the payment of his final bill shall not be made.  The Contractor shall be made liable to pay for the use and occupation at the rates to be determined by the Engineer if the Contractor over stays in the land after the Contract is completed.

51.	ELECTRICITY:

The Contractor will make necessary arrangements for erection of his site office and site stores after getting written permission from the employer to erect such temporary structure at his own cost.  Temporary power supply will be provided at one point at the nearest switch room. The power consumption charges will have to be borne by the Contractor.  However, non-availability of the Crane does not leave the contractor off his responsibilities

52.	WATER

The contractor is permitted to make use of water source available at office sites for construction purpose. Transport of water from the source to the working areas will be contractor’s responsibility.

53.	FACILITIES TO BE PROVIDED BY THE CONTRACTOR

53.1	Machinery, Tools, tackles and scaffoldings

The Contractor shall provide the required machinery/equipment, accessories, necessary tools and tackles, scaffoldings, instruments, and all the normal consumable materials required for the satisfactory execution of this contract. The Contractor shall arrange for cranes for unloading and erection purpose, if required. He shall submit a list of all such materials to the Engineer before the commencement of pre-assembly at Site. These tools and tackles shall not be removed from the Site without the written permission of the Engineer.

53.2 Gate Pass for Materials:

All tools, tackles, construction materials, welding materials etc., will be taken inside the site limits only after registration with security personnel.  Also any material will be taken out only on valid gate pass issued by purchaser’s representative after checking the proper “IN” gate passes.  The contractor shall have to preserve the “IN” gate passes obtained from security when every /any material is route inside the site to enable taking back the balance/excess materials, Tools and Tackles after completion of works.

53.2	Communication

The Employer will extend the telephone and telex facilities, if available at Site, for purposes of Contract. The Contractor shall be charged at actual for such facilities.

53.3 	First-aid

53.3.1 The Contractor shall provide necessary first-aid facilities for all his employees, representatives and workmen working at the Site. Enough number of Contractor`s personnel shall be trained in administering first-aid.

53.4	Cleanliness

53.4.1 The Contractor shall be responsible for keeping the entire area allotted to him clean and free from rubbish, debris etc. during the period of Contract. The Contractor shall employ enough number of special personnel to thoroughly clean his work-area at least once in a day. All such rubbish and scrap material shall be stacked or disposed off in a place to be identified by the Engineer.  Materials and stores shall be so arranged to permit easy cleaning of the area.  In areas where equipment might drip oil and cause damage to the floor surface, a suitable protective cover of a flame resistant, oil proof sheet shall be provided to protect the floor from such damage.

53.4.2 Similarly the labour colony, the offices and the residential areas of the Contractor’s employees and workmen shall be kept clean and neat to the entire satisfaction of the Engineer. Proper sanitary arrangement shall be provided by the Contractor, in the work-areas, office and residential areas of the Contractor

54.	LINES AND GRADES

All the works shall be performed to the lines, grades and elevations indicated on the drawings. The Contractor shall be responsible to locate and layout the works. Basic horizontal and vertical control points will be established and marked by the Engineer at site at suitable points. These points shall be used as datum for the works under the Contract. The Contractor shall inform the Engineer well in advance of the times and places at which he wishes to do work in the area allotted to him so that suitable datum points may be established and checked by the Engineer to enable the Contractor to proceed with his works. Any work done without being properly located may be removed and/or dismantled by the Engineer at Contractor’s expense.

55	SECURITY

The Contractor shall have total responsibility for all equipment and materials in his custody/stores, loose, semi-assembled and/or erected by him at Site. The Contractor shall make suitable security arrangements including employment of security personnel to ensure the protection of all materials, equipment and works from theft, fire, pilferage and any other damages and loss. All materials of the Contractor shall enter and leave the project site only with the written permission of the Engineer in the prescribed manner.

56.	CONTRACTOR’S AREA LIMITS

The Engineer will mark-out the boundary limits of access roads, parking spaces, storage and construction areas for the Contractor and the Contractor shall not trespass the areas not so marked out for him. The Contractor shall be responsible to ensure none of his personnel move out of the areas marked out for his operations. In case of such a need for the Contractor’s personnel to work out of the areas marked out for him, the same shall be done only with the written permission of the Engineer.

57.	CONTRACTOR’S CO-OPERATION WITH THE EMPLOYER

In case where the performance of the erection work by the Contractor affects the operation of the system facilities of the Employer, such erection work of the Contractor shall be scheduled to be performed only in the manner stipulated by the Engineer and the same shall be acceptable at all times to the Contractor. The Engineer may impose such restrictions on the facilities provided to the Contractor such as electricity, water, etc. as he may think fit in the interest of the Employer and the Contractor shall strictly adhere to such restrictions and co-operate with the Engineer. It will be the responsibility of the Contractor to provide all necessary temporary instrumentation and other measuring devices required during start-up and operation of the equipment systems, which are erected by him. The Contractor shall also be responsible for flushing and initial filling of all the oil and lubricants required for the equipment furnished and erected by him, so as to make such equipment ready for operation. The Contractor shall be responsible for supplying such flushing oil and other lubricants unless otherwise specified elsewhere in the document and specifications.

58.	PRE-COMMISSIONING TRIALS AND INITIAL OPERATIONS

The pre-commissioning trials and initial operations of the equipment furnished and erected by the Contractor shall be the responsibility of the Contractor as detailed in relevant clauses in Technical Specifications Section. The Contractor shall provide, in addition, test instruments, calibrating devices, etc and labour required for successful performance of these trials. If it is anticipated that the above test may prolong for a long time, the Contractor’s workmen required for the above test shall always be present at Site during such trials.

59.	MATERIALS HANDLING AND STORAGE

59.1	All the equipment furnished under the Contract and arriving at Site shall be promptly received, unloaded, transported and stored in the storage spaces by the Contractor.

59.2	Contractor shall be responsible for examining all the shipment and notify the Engineer immediately of any damages, storage, discrepancy etc, for the purpose of Engineer’s information only. The Contractor shall submit to the Engineer every week a report detailing all the receipts during the week. However, the Contractor shall be solely responsible for any shortages or damages in transit, handling and/ or in storage and erection of the equipment at Site. Any demurrage, wharfage and other such charges claimed by the transporters, railways etc, shall be to the account of the Contractor.

59.3	The Contractor shall maintain an accurate and exhaustive record detailing out the list of all equipment received by him for the purpose of erection and keep such record open for the inspection of the Engineer in-charge.

59.4	All equipment shall be handled very carefully to prevent any damage or loss. No bare wire ropes, slings, etc. shall be used for unloading and/or handling of the equipment without the specific written permission of the Engineer. The equipment stored shall be properly protected to prevent damage either to the equipment or to the floor where they are stored. The equipment from the store shall be moved to the actual location at the appropriate time so as to avoid damage of such equipment at Site.

59.5	All electrical panels, control gears, motors and such other devices shall be properly dried by heating before they are installed and energized. Motor bearings, slip ring, commutators and other exposed parts shall be protected against moisture ingress and corrosion during storage and periodically inspected.

59.6	All the electrical equipment such as motors, generators, etc. shall be tested for insulation resistance at least once in three months from the date of receipt till the date of commissioning and a record of such measured insulation values maintained by the Contractor. Such records shall be opened for inspection by the Engineer.

59.7	The Contractor shall ensure that all the packing materials and protection devices, used for various equipment during transit and storage, are removed before the equipment are installed.

59.8	The consumable and other supplies likely to deteriorate due to storage must be thoroughly protected and stored in a suitable manner to prevent damage or deterioration in quality by storage.

59.9	All the materials stored in the open or dusty location must be covered with suitable weatherproof and flame proof covering material wherever applicable.

59.10	If the materials belonging to the Contractor are stored in areas other than those earmarked for him, the Engineer will have the right to get it moved to the area earmarked for the Contractor at the Contractor’s cost.

59.11	The Contractor shall be responsible for making suitable indoor storage facilities to store all equipment, which require indoor storage.  Normally all the electrical equipment such as motors, control gears, generators, exciters and consumables like electrodes, lubricants etc. shall be stored in the closed storage space.  The Engineer, in addition, may direct the Contractor to move certain other materials, which in his opinion will require indoor storage, to indoor storage areas, which the Contractor shall strictly comply with.

60.	INDEMNITIES

The contractor is liable for and indemnifies the APSPDCL against losses, expenses and claims for loss or damage to physical property, personal injury and death caused by his own acts or omissions.

60.1	The contractor claiming indemnity is to take all reasonable steps to mitigate the lower damage will occur.

60.2	The contractor indemnifies the APSPDCL against claims to damages caused by the movements of his equipment or temporary works.

60.3	The Contractor shall submit an “Indemnity Bond” to the APSPDCL incorporating the above points before taking up the execution of the work.

61.	CONSTRUCTION MANAGEMENT

61.1	The field activities of the Contractors working at Site, will be coordinated by the Engineer and the Engineer’s decision shall be final in resolving any disputes or conflicts between the Contractor and other Contractors and the tradesmen of the Employer regarding scheduling and coordination of work.  Such decision by the Engineer shall not be a cause for extra compensation or extension of time for the Contractor.

61.2	The Engineer shall hold weekly meetings of all the Contractors working at Site, at a time and place to be designated by the Engineer.  The Contractor shall attend such meetings and take notes of discussions during the meeting and the decision of the Engineer and shall strictly adhere to those decisions in performing his works. In addition to the above weekly meeting, the Engineer may call for other meetings either with individual Contractors or with selected number of Contractors and in such a case the Contractors if called, will also attend such meetings.

61.3	Time is the essence of the Contract and the Contractor shall be responsible for performance of his works in accordance with the specified construction schedule. If at any time, the Contractor is falling behind the schedule, he shall take necessary action to make good for such delays by increasing his work force or by working overtime or otherwise accelerate the progress of the work to comply with the schedule and shall communicate such actions in writing to the Engineer, satisfying that his action will compensate for the delay. The Contractor shall not be allowed any extra compensation for such action.

61.4	The Engineer shall, however, not be responsible for provision of additional labour and/or materials or supply or any other services to the Contractor except for the coordination work between various Contractors as set out earlier.

62.	FIELD OFFICE RECORDS

The Contractor shall maintain at his Site office up to date copies of all drawings, specifications and other Contract Documents and any other supplementary data complete with all the latest revisions thereto.  The Contractor shall also maintain in addition the continuous record of all changes to the above Contract Documents, drawings, specifications, and supplementary data, etc. effected at the field and on completion of his total assignment under the Contract shall incorporate all such changes on the drawings and other Engineering data to indicate as installed conditions of the equipment furnished and erected under the Contract.  Such drawings and Engineering data shall be submitted to the Engineer in required number of copies.

63.	CONTRACTOR’S MATERIALS BROUGHT ON TO SITE

63.1	The Contractor shall bring to Site all equipment, components, parts, materials, including construction equipment, tools and tackles for the purpose of the works under intimation to the Engineer.  All such goods shall, from the time of their being brought vest in the Employer, but may be used for the purpose of the works only and shall not on any account be removed or taken away by the Contractor without the written permission of the Engineer.  The Contractor shall nevertheless be solely liable and responsible for any loss or destruction thereof and damage thereto.

63.2	The Employer shall have a lien on such goods for any sum or sums which may at any time be due or owing to him by the Contractor, under, in respect of or by reasons of the Contract.  After giving a fifteen (15) days notice in writing of his intention to do so, the Employer shall be at liberty to sell and dispose off any such goods, in such manner as he shall think fit including public auction or private treaty and to apply the proceeds in or towards the satisfaction of such sum or sums due as aforesaid.

63.3	After the completion of the Works, the Contractor shall remove from the Site under the direction of the Engineer the materials such as construction equipment, erection tools and tackles, scaffolding etc. with the written permission of the Engineer.  If the Contractor fails to remove such materials, within fifteen (15) days of issue of a notice by the Engineer to do so then the Engineer shall have the liberty to dispose off such materials as detailed under Clause 29.2 above and credit the proceeds thereto to the account of the Contractor.

64.	PROTECTION OF PROPERTY AND CONTRACTOR’S LIABILITY

64.1	The Contractor shall be responsible for any damage resulting from his operations.  He shall also be responsible for protection of all persons including members of public and employees of the Employer and the employees of other Contractors and Sub-Contractors and all public and private property including structures, building, other plants and equipment and utility either above or below the ground.

64.2	The Contractor will ensure provision of necessary safety equipment such as barriers, signboards, warning lights and alarms, etc. to provide adequate protections to persons and property.  The Contractor shall be responsible to give reasonable notice to the Engineer and the Employer of public or private property and utilities when such property and utilities are likely to get damaged or injured during the performance of his works and shall make all necessary arrangements with such Employers, related to removal and/ or replacement or protection of such property and utilities.

65.	PAINTING

All exposed metal parts of the equipment including piping, structures, railing etc. wherever applicable, after installation unless otherwise surface protected, shall be first painted with at least one coat of suitable primer which matches the shop primer paint used, after thoroughly cleaning all such parts of all dirt, rust, scales, grease, oil and other foreign materials by wire brushing, scraping or sand blasting and the same being inspected and approved by the Engineer for painting. Afterwards, the above parts shall be finished painted with two coats of allowed resin machinery enamel paints. The quality of the finish paint shall be as per the standards of ISI or equivalent and shall be of the colour as approved by the Engineer.

66.	INSURANCE

66.1	In addition to the conditions covered under the Clause entitled ‘Insurance’ in General Terms and Conditions of Contract of this Volume-I, the following provisions will also apply to the portion of works to be done beyond the Contractor’s own or his Sub-Contractor’s manufacturing Works. Insurance coverage for all materials and men (involved in the work) shall be at the risk & cost of the contractor.

66.2	WORKMEN’S COMPENSATION INSURANCE

This insurance shall protect the Contractor against all claims applicable under the Workmen’s Compensation Act, 1948 (Government of India). This policy shall also cover the Contractor against claims for injury, disability, disease or death of his or his Sub-Contractor’s employee, which for any reason are not covered under the Workmen’s Compensation Act, 1948. The liabilities shall not be less than:

Workmen’s      :	As per statutory Compensation Provisions

Employee’s	 :	As per statutory liability Provisions

67.	UNFAVOURABLE WORKING CONDITIONS

The Contractor shall confine all his field operations to those works, which can be performed without subjecting the equipment and materials to adverse effects during inclement weather conditions, like monsoon, storms etc. and during other unfavorable construction conditions. No field activities shall be performed by the Contractor under conditions, which might adversely affect the quality and efficiency thereof, unless special precautions or measures are taken by the Contractor in a proper and satisfactory manner in the performance of such Works and with the concurrence of the Engineer. Such unfavorable construction conditions will in no way relieve the Contractor of his responsibility to perform the Works as per the schedule.

68.	CHECK OUT OF CONTROL SYSTEMS

After completion of wiring, cabling furnished under separate specification and laid and terminated by the Employer, the Contractor shall check out the operation of all control system for the equipment furnished and installed under these specifications and documents.

69.	CABLING

69.1	All cables shall be supported by conduits or cable trays run in air or in cable channels. These shall be installed in exposed runs parallel or perpendicular to dominant surface with right angle turn made of symmetrical bends for fittings. When cables are run on cable trays, they shall be clamped at minimum intervals of 2000 mm or otherwise as directed by the Engineer.

69.2	Each cable, whether power or control, shall be provided with a metallic or plastic tag of an approved type, bearing a cable reference number indicated in the cable and conduit list (prepared by the Contractor), at every 5 metre run or part thereof and at both ends of the cable adjacent to the terminations. Cable routing is to be done in such a way that cables are accessible for any maintenance and for easy identification.

690.3	Sharp bending and kinking of cables shall be avoided. The minimum radii for PVC insulated cables 1100 V grade shall be 15D where D is the overall diameter of the cable. Installation of other cables like high voltage, coaxial, screened compensating, mineral insulated shall be in accordance with the cable manufacturer’s recommendations. Wherever cables cross roads and water, oils, sewage or gas lines, special care should be taken for the protection of the cables in designing the cables channels.

69.4	In each cable run some extra length shall be kept at a suitable point to enable one or two straight through joints to be made, should the cable develop fault at a later date.

69.5	Control cable terminations shall be made in accordance with wiring diagrams, using identifying codes subject to Engineer’s approval. Multi-core control cable jackets shall be removed as required to train and terminate the conductors. The cable jacket shall be left on the cable, as far as possible, to the point of the first conductor branch. The insulated conductors from which the jacket is removed shall be neatly twined in bundles and terminated. The bundles shall be firmly, but not tightly, tied utilizing plastic or nylon ties or specially treated fungus protected cord made for this purpose. Control cable conductor insulation shall be secure and even.

69.6	The connectors for control cables shall be covered with a transparent insulating sleeve so as to prevent accidental contact with ground or adjacent terminals and shall preferably be terminated in elmex terminals and washers. The insulating sleeve shall be fire resistant and shall be long enough to over pass the conductor insulation. All control cables shall be fanned out and connection made to terminal blocks and test equipment for proper operation before cables are corded together.

70.	SUPPLY OF MATERIALS BY THE CONTRACTOR:

The contractor has to make his own arrangements for procurement, supply and use of all the materials necessary for the execution of the project on turnkey basis as per Annexure-1A and compliance of the following should be ensured.

- These materials should conform to the relevant Indian Standard specification.  These materials shall be supplied at-least one month in advance of their requirement manufactures test certificate for these materials shall be submitted and got approved by Engineer before utilization.  The materials so supplied by the contractor shall be guaranteed by him for satisfactory performance up-to the end of the maintenance and defects liability period.

- All materials to be supplied should fully conform to provisions under clause 3 of Instructions to Bidders.

- In procurement of these items the contractor shall follow all regulations of the APSPDCL/Government of India in respect of import license etc., if he chooses to procure these from imports.  Further, the contractor shall be responsible for the payment of applicable duties and taxes, port clearance inland transportation etc.

71  PREAMBLE

71.1 	The rates and prices tendered in the price bid document shall, except in so far as it is otherwise provided under the Contract, include all constructional plant, labour, supervision materials, erection maintenance, insurance, profit.  Taxes and duties, together with all general risks, liabilities and obligations set out or implied in the contract.

72    QUALITY ASSURANCE PLAN

72.1.	To ensure that the equipments are in accordance with the specifications, the contractor shall adopt suitable quality assurance programme to control such activities at all points, as necessary. Such programme shall be out lined by the contractor and shall be finally accepted by owner/ authorized representative after discussions before the award of contract. The QA programme shall be generally in line with mentioned in bid.

72.2	The bidder shall also furnish copies of the reference documents/ plant standard / acceptance norms/ test and inspection procedure etc., as referred in Quality Plan alongwith Quality Plans.

72.3	All materials used and supplied shall be accompanied by valid and approved materials certificates and tests and inspection reports. These certificates and reports shall indicate the heat numbers or other such acceptance identical numbers of the material. The material certified shall also have the identification details stamped on it.

73.	 DISPUTES

24.1	If the Contractor believes that a decision taken by the Engineer was whether outside the authority given to the Engineer by the Contract or that the decision was wrongly taken, the decision shall be referred to the Arbitrator within 14 days of the notification of the Engineer’s decision.

74.	 PROCEDURE FOR DISPUTES

74.1	The arbitration shall be conducted in accordance with provisions of Indian Arbitration Act 1996 and at the place shown in the Contract Data. The language in which arbitration will be effected is English.

75  COMPLETION CERTIFICATE

75.1 The contactor shall submit Completion Report of the project to Owner. The Completion Report shall consist of the following documents:

(i) Copy of the Commissioning Certificate of Solar Power plant.

(ii) Technical documents as per scope of work & technical specifications according to which the work has carried out.

 Four sets of as built drawings showing therein modification and corrections, if any, made during the course of execution signed by the Contactor. A soft copy of as built drawings shall also be submitted.

 Copy of complete layout of the solar array including Evacuation system.

 Copies of test Certificates for type / routine tests performed on major equipment.

 O&M Manuals – 3 sets

 Copies of Statutory clearances / permissions.

 Certificate / undertaking for making payment of all statutory requirements, duties, labour wages and others for having made payment.

 An undertaking confirming the payment of all statutory duties, taxes or document (s) having evidence of paying statutory duties, taxes etc. as per requirement of concerned statutory authorities.

 Certificate regarding completion of the facility in all respect by the Engineer In Charge/ Consultants

75.2 Owner shall issue Completion Certificate after verifying from the completion documents and satisfying itself that the work has been completed in accordance with details set out in the construction and erection drawings and the contract documents. No Completion Certificate shall be given nor shall the work be deemed to have been executed until the export of generated Solar power commenced to LT BUS , statutory requirements are completed and all scaffolding, surplus materials and rubbish is cleaned off the site completely.

DETAILS OF EARNEST MONEY DEPOSIT

ANNEXURE – 1

(Separately typed preferable computerized and On Tenderer Letter head)

Ref. No.  NO. CGM/PROJECTS/SPDCL/TPT/SIP-01/2013-14	Date

To,

The Chief General Manager/Projects

APSPDCL:: Tirupati

Subject: Earnest Money Deposit (EMD) for the Tender No. NO. F. CGM/PROJECTS/SPDCL/TPT/SIP-01/2013-14

Respected Sir,

I/ We  	(hereinafter referred to as the  Tenderer) being desirous of Biding for the work under the above mentioned Tender document and having fully understood the nature of the work and having carefully noted all the terms and conditions, specifications etc., as mentioned in the Tender document.

I / We feel an immense pleasure to quote our most competitive rates herewith duly signed by me / us. I / We have quoted separately for the systems and the Earnest Money Deposit / s has been submitted separately in Envelop 1;

EMD details

Amount (Rs.)	:

Instrument Number  :

Date of issuance	:

Name of the Bank:

Place:	(Signature of Tenderer)

Name :

Designation :

Date:	Seal :

TENDERER’S GENERAL INFORMATION

(To be typed separately & submitted  )

To,

The Chief General Manager/Projects

APSPDCL:: Tirupati

Subject : Tender No. CGM/PROJECTS/SPDCL/TPT/SIP-01/2013-14 for

1.	Name of Tenderer

2.	Status of Firm

3.	Number of Years in Operation

4.	Registered Address

5.	Operating Address

(if different from above.)

6.	Telephone Number

[Area Code]	[Number]

7.	E-mail Address & Web Site

8.	Tele-fax Number

[Area Code]	[Number]

9.	PAN [Number]

10.	Service Tax Number

[Enclosed Copy of ‘PAN CARD’] [Enclosed copy of ‘Service Tax Registration Certificate]

(Signature of Tenderer)

Date	Name :

Designation :

Place :	Seal :

DECLARATION

(To be submitted on Rs.100/- stamp paper)

ANNEXURE – 2

I  /  We,  hereby  declare  that  I  /  We  have  made  myself  /  ourselves  thoroughly conversant with the sub – soil conditions, local conditions regarding all materials and Labour of which I / we have based my / our rates of this work. The specifications, conditions and lead of materials on this work have been carefully studied and understood by me / us before submitting this Tender. I / We undertake to use only the best materials defined / approved by the Ministry of New and Renewable Energy (MNRE) GoI.

The systems will be provided as per the specifications and guidelines issued by the Ministry of New and Renewable Energy / APSPDCL. We are bound to adhere the guidelines issued by the  Ministry of New and Renewable Energy / APSPDCL from time to time. We also hereby committed that  if  in future MNRE make any changes in the specifications of the systems the same will be incorporated in the present Tender projects. We hereby agree that the work will be executed within the cost of Tender mentioned in the financial bid and there will be no escalation in cost for any reason thereof. We also agree that if we fail to complete the work and drop the work in middle,   APSPDCL shall have right to recover the full amount from us. I / We shall accept any amendments made by APSPDCL from time to time during total project completion period including 5 years Comprehensive maintenance contract (CMC).

I / We am/are also committed that we shall complete the work within stipulated time period specified in the work order for any work assigned by Order Issuing Organization. We will not ask for any further time extension.

I / We am / are bound to work as per Tender and work Order issued by APSPDCL for this work with 5 years Comprehensive Maintenance Contract. In case of failure of the same, we shall be  responsible for any loss and for the action taken by competent Authority of APSPDCL resulting to ban to work and black-listing.

I / We shall comply with the provision of Contract Labour. (Regulation and Abolition) Act   1970,  Minimum  Wages  Act.  1948,  Payment  of  Wages  Act.  1963,  Workmen’s Compensation Act. 1961, the Contract Labour (Regulation and Abolition) Act, 1979 and all other related Acts and any modification thereof or any law relating there to and rules made there under from time to time. APSPDCL shall not be responsible in this regard.

I / We shall be wholly responsible for any accident or any unusual/ unexpected circumstances held during the execution of work & also during the CMC period of 5 years.

(Signature of Tenderer)

Date	Name :

Designation :

Place :	Seal :

ANNEXURE - 3

COMPANY PROFILE

(To be typed separately & submitted in Envelope No.1)

| A} Information : |  |
| --- | --- |
| Name of Company : |  |
| Address of Head Office : |  |
| Contact Person : |  |
| Telephone : |  |
| Telefax : |  |
| E-Mail : |  |
| No. of Branches (Dealers) and their address |  |
| Address for Correspondence : |  |
| Contact Person : |  |
| Telephone : |  |
| Telefax : |  |
| E-mail : |  |
| B} Business Organization : (Please tick wherever applicable & attach all supporting documents) |  |
| Sole proprietorship |  |
| Private Limited |  |
| Public Sector Undertaking |  |
| Limited Company |  |
| Joint Venture |  |
| Others (Please Specify Status) |  |
| C} Business Management : |  |
| Attach Corporate Organization Chart with Name |  |
| D} Total Number of Employees Employed : |  |
| 1) At Head Office |  |
| 2) At Branch Office |  |
| 3) At Site |  |
| E} Is Your Organization a Subsidiary of Another Company ? | Yes/ No |
| If Yes, of whom? |  |
| F} Financial Capability : |  |
| Annual Turnover Last 5 Years : Attach Balance sheets of last 3 years. Rs. In Lakhs |  |
| Projected this year |  |
| Last year |  |
| One year before last year |  |
| Two year before last year |  |
| Three year before last year |  |
| Four year before last year |  |
| Name and address of the bankers with Contact person and contact numbers. |  |
| G} Whether your company hold following certificates: | Yes/ No |
| ISO 9001-2000 |  |
| ISO 14001-1996 |  |
| OHSAS – 18001-1999 |  |
| If No, do you substantiate a need to have them | Yes/ No |
| H} Are there any Litigations/ Court cases against your company? | Yes/ No |
| If yes, give details : |  |
| I} Any other information that you want to give (may attach separate pages) |  |

Annexure-4

STAFF DETAILS

| Name of the Organization : |  |  |  |  |
| --- | --- | --- | --- | --- |
| List of staff having relevant work experience |  |  |  |  |
| Sr. No. | Name | Qualification | Designation | Total Experience in years |

Annexure-5

DRAFT ACTIVITY CHART

Bidder shall furnish Bar Chart for the following activities and his plan for implementation of the project to meet the completion date. This information shall be in addition to detailed project schedule and other information he is required to furnish as part of his offer. The activities indicated herein are minimum activities for which bidder shall furnish the required information. Bidders are encouraged to furnish more detailed information in their offer.

| S.No | Description | Start Time | Completion Time |
| --- | --- | --- | --- |
| 1 | Site clearing |  |  |
| 2 | Design of structures, foundation and other associated, overall plant design and drawings , submission to SPDCL and arranging approval from SPDCL |  |  |
| 3. | Preparation of project report Application to State Nodal Agency for approval of Subsidy from MNRE Arranging sanction of funds from MNRE through RREC |  |  |
| 4 | Construction of store shade foundations of module structures |  |  |
| 5 | Clearance from pollution control /Aviation Department, any other statuary approval /Clearances as applicable |  |  |
| 6 | Supply of modules , mounting structures Equipments and Materials |  |  |
| 7 | AC Distribution Board , D C distribution Board , Power and control Cables and Balance items of Solar Plant |  |  |
| 8 | Supply of balance materials |  |  |
| 9 | Erection of material |  |  |
| 10 | Commissioning of Plant |  |  |
| 11 | Completion of plant in all respect |  |  |

WORK EXPERIENCE

ANNEXURE - 6

| Name of the Organization : |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| List of works Completed in Last 3 Years |  |  |  |  |  |  |  |  |
| Sr. No. | Name of the Project | Name & Address of the Client | Contact Telephone Numbers of the Client | Major Items of Work* | Value of Work in Rs. | Start Date | Due Date of Completion | Actual completion Date |

Note : 1. If Actual completion date is beyond the Schedule completion Date, please give reasons for the delay.

2. Attach relevant completion certificates document for works in previous 3 years separately.

Authorized Signatory

Company Seal

Date : Place :

ANNEXURE-7

### DECLARATION

I / WE ……………………………………………………………….  have gone through carefully all the Tender conditions and solemnly declare that  I / we will abide by any penal action such as disqualification or black listing or determination of contract or any other action deemed fit, taken by, the Department against us, if it is found that the statements, documents, certificates produced by us are  false / fabricated.

I / WE hereby declare that, I / WE have not been blacklisted / debarred / Suspended / demoted in any department in Andhra Pradesh or in any State due to any reasons.

Signature of the Bidder

ANNEXURE –8

FINANCIAL BID (to be uploaded online only) for

Design, Supply, Installation, Testing, Commissioning With Five Years of Comprehensive Maintenance Contract (of 100 kWp Solar Photovoltaic Power Plant In APSPDCL

The cost details for 100 kWp Solar PV power plant should be submitted as follows:

| Sr. No. | Name of work | Capacity | Cost of SPV Power Plant (Cost of Material + Cost of installation and commissioning, testing with 5 yrs. CMC (O&M (including manpower)) as per tender document including relevant manpower) (Rs.) (in figures) |
| --- | --- | --- | --- |
| 1. | Design, Supply, Installation, Testing, Commissioning With Five Years of Comprehensive Maintenance Contract (O&M and man power) Of 100 kWp Solar Photovoltaic Power Plant In APSPDCL AS PER TENDER DOCUMENT | 100 kWp |  |

Rupees (in words) ……………………………………………………………….

Cost is inclusive of all taxes,duties, insurance, octroi, transportation, loading, unloading, design, installation, commissioning and testing, O & M (including manpower) and CMC for 5 years.

NOTE: The tenderes should upload additional PDF file on-line for the detailed item- wise,   work-wise, CMC break-up  along  with  applicable  taxes & duties  with  the  price  bid.  However, the bids will be evaluated on the basis of consolidated price bid as above.

(DO NOT SUBMIT FINANCIAL BID IN PHYSICAL FORM, TO BE UPLOADED ONLINE ONLY)

(Signature of Tenderer)

Date	Name :

Designation :

SYSTEM PHILOSOPHY

1.1 SOLAR SYSTEM AND COORDINATION WITH EXISTING SYSTEM

1.1.1 The SPV array generally consisting of number of SPV modules that directly produces DC electricity power on receipt of solar irradiation. This DC power is converted to AC power by PCUs. The AC output of 100 kW solar plant at 415 V level will work in combination with Discom feed existing LT System of APSPDCL office at Tirupati. These modules usually are made up of SPV cells, forming the basic building block of a solar array. Modules may be connected in series or parallel to increase the voltage and current, and thus achieve the required solar array characteristics that will match the load.

1.1.2 The bidder shall design the system in such a way that System controller of PSU should have ability to harvest the maximum possible Solar Power generation to be utilized for energy requirement of APSPDCL office at Tirupati. During holidays/Sunday/Saturday when the consumption may be low in APSPDCL office, the part of generated energy will be fed to Discom L T Grid.

1.2 The main objective is the high availability and reliability of the plant. In order to achieve the main objective, the following principles shall be adopted while designing system.

a) 	Technology: Solar PV crystalline cells of high efficiency and the modules should be manufactured in India so as to meet MNRE Guidelines. APSPDCL will avail subsidy for solar plant from MNRE as such bidder should use the modules and other material which is eligible for such subsidy.

b) 	The Stabilized output of solar Power plant shall be 100kWp after one year (measured at standard test conditions of solar radiation of 1000W per sq meter).

The bidder shall demonstrate the capacity of plant after one year from date of commissioning of plant.

 The bidder shall use adequate capacity of SPV module, PCUs, Junction boxes etc to ensure generation of power as per design estimates. This is to be done by applying liberal de-rating factors for the array and recognizing the efficiency parameters of PCUs, transformers, etc.

 The output at Invertors (s) will be considered for verification purpose. Bidder should indicate procedure and details of software or formula for demonstration of capacity of plant in tender itself. For other purpose the meter reading will be considered.

c)	Use of equipment and systems with proven design and performance that have a high availability track record under similar service conditions.

d) 	Selection of the equipment and adoption of a plant layout to ensure ease of maintenance.

e) 	Strict compliance with the approved and proven quality assurance norms and procedures during the different phases of the project.

f) 	Proper monitoring in the synchronizations which ensures the availability of power to the grid. Generation voltage of 415V has to fed to grid voltage at the point of interconnection.

g) 	The injection of DC power in to Grid shall be avoided by using suitable isolation transformer etc at output of inverter.

h) 	Ripple content must not exceed 3% on DC side

i) 	Limits for harmonics as per CEA technical standard on Grid connectivity are as follow :

Total voltage harmonics distortion not more than 5%

Individual voltage harmonics distortion not more than 3 %

Total current harmonics distortion not more than 8%

j) 	The power plant has to operate in parallel with the grid system which is infinite electrical system. Any faults not taken care will result in damage of only SPV power plant without effecting DISCOMS infinite system. Thus the Solar Power Plant has to protect its equipment against any of possible fault or other disturbances from the grid.

k) 	Very fast microprocessor based Directional and Reverse power flow protection should be provided to insure isolation of the solar power plant from the grid at the time of any fault or/and any additional suitable protection.

1.2 	The basic and detailed engineering of the plant will aim at achieving high standards of operational performance especially considering following:

a. Optimum availability of modules during the day time.

b. Ensuring module layout to prevent shading.

c. Selection of PCUs with high track record and readily availability of requisite spares.

d. Careful logging of operation data / historical information from the Data Monitoring Systems, and periodically processing it to determine abnormal or slowly deteriorating conditions.

e. SPV power plant should be designed to operate satisfactorily in parallel with the Discom Grid within permissible limits of high voltage and frequency fluctuation conditions, so as to export the maximum possible units to the grid.

f. Flat plate arrays are held fixed at a tilted angle and face towards the equator, are most common. The angle of tilt should be approximately equal to the angle of latitude for the site. A steeper angle increases the output in winter; while a shallower angle more output in summer. It should be arranged in such a manner that optimize generation is achieved.

g. Based on the Solar Insolation data, the solar PV system should be so designed that it shall take into account the mean energy output after allowing for various losses, temperature corrections, on an average day for each month of the year.

h. Bidder should use the modules and other material which is eligible for subsidy from MNRE.

i. The offered Grid Connected Solar Power Plant should be able to generate power through solar energy and supply clean and green electricity to the grid

1.3 The specification provided with this bid document is a functional one; the design provided in this document is only meant as an example. The Bidder/ must submit a proposal based upon their own design. In order to win the Contract the Bidder/ must optimize their own design for Solar Photovoltaic (SPV) proven technology so that it best meets the evaluation criteria given in this bid document. The bidders are advised to visit the site before designing the plant and offer their bid. The bidders are also required to incorporate all the system required for efficient operation of 100 kW solar Plant in parallel with Discom supply.

1.4 The supplier/manufacturer shall submit the detail design of the complete solar generating system by using their software to optimize the combination of modules considering the specific location, isolation, nature of load etc

TECHNICAL SPECIFICATION

The general  scope  under  this  contract  includes  to  design,  manufacture, testing ,inspection, packing and forwarding, transportation upto project site, loading & unloading, storage in safe custody, erection, carrying out preliminary tests at site, commissioning, performance  testing,  operation  and  maintenance  for  5  years  & handing  over to the purchaser all the equipment installed for 100KWP   SPV Power plant at APSPDCL, Tirupati.

The  illustrative  Schedule  of  requirements  is  in  accordance  with  the specifications contained in this document

1.1	System Details:

| Sl. No. | Brief Description |  | Units | Make |  |
| --- | --- | --- | --- | --- | --- |
| 1 | SPV modules for a total capacity of 100KWp as per specifications. |  | 1 Set | BHEL/ CEL/ REIL/ TATA BP/ PHOTON/Moserbare/TITAN/SHAN |  |
| 2 | SPV module mounting structure suitable for accommodating 100 KWp capacity SPV modules including foundation as per specifications on roof top (Terrance) |  | 1 Set |  |  |
| 3 | PCUs as per specifications |  | 1 No./ Set | SMA/ SCHENIEDER- XENTREX/ SEMICRON/ ABB/ PPS / OPS/ DB Electronics |  |
| 4 | Array Junction Boxes |  | 1 Set | Tyco / Hensel/ Spelberg |  |
| 5 | Main Junction Boxes |  | 1 Set | Tyco / Hensel/ Spelberg |  |
| 6 | Data Logging system with remote monitoring as per specification |  | 1 Set | system as per specifications |  |
| 7 | DC Distribution units as per specifications |  | 1 Set | Siemens / ABB / Schnieder Electric/L&T /Havells/HPL |  |
| 8 | AC Distribution units as per specifications |  | 1 Set | Siemens / ABB / Schnieder Electric/L&T/ Havells/HPL |  |
| 9 | Cables requirement as per design |  | Mtrs. As required at site for full plant commissio ning | Finolex /Polycab/ Havells/HPL |  |
| 10 | Fire extinguisher in accordance with BIS codes for electrical short circuit fires along with sand buckets | 1 Set |  |  |  |
| 11 | Lightning arrester complete set as per specification | 1 Set |  |  |  |
| 12 | Earthing complete set as per specification | 1 Set |  |  |  |
| 13 | Spares, tools and plant for 5 years operation and maintenance | As per list |  |  |  |
| 14 | Fuses, Transfer switches, Printed Circuit boards required for power plant | 1 Set |  |  |  |
| 15 | Providing training to engineers and site staff for operating Maintenance and trouble shooting skills | 1 Item |  |  |  |
| 16 | Operation and maintenance of the SPV Power Plant for a period of 5 years from date of commissioning of the power plant. | 1 Item |  |  |  |
| 17 | Engineering, electrical drawings and installations and O&M manuals | 1 Sets |  |  |  |
| 18 | Any other equipment required to complete the installation |  |  |  |  |

All the items against which no make has been mentioned must confirm to ISI

standards.

The SPV Power plant shall have a total capacity of 100 kWp. Further, to make  system cost effective and feasible it should be grid connected without any backup.

1.2	SOLAR PHOTOVOLTAIC MODULES

1.2.1 The total solar PV array capacity should not be less than 100 kWp and should  comprise  of  solar  crystalline  modules  of  minimum  250  Wp  and  above wattage. Module capacity less than minimum 250 watts should not be supplied. The module type must be qualified as per IEC 61215 latest edition for crystalline silicon. SPV module  conversion efficiency should be equal to or greater than 15% under STC. Modules must qualify to IEC 61730 Part I and II for safety qualification testing. Certificate for module qualification from IEC or equivalent to be submitted as part of the bid offer. Self undertaking from manufacturer / supplier that the modules being supplied are as per above.

1.2.2	The PV module shall perform satisfactorily in humidity up to 100% with temperature between – 40 C to + 85 C. Since the modules would be used in a high voltage circuit, the high voltage insulation test shall be carried out on each module and a test certificate to that effect provided and they have highly corrosive atmosphere throughout their Lifetime and they must qualify to IEC 61701.

1.2.3 The predicted electrical degradation of power generated not exceeding 20% of the minimum rated power over the 25 year period and not more than 10% after ten years period of the full rated original output (As per MNRE Standards).

1.2.4 Other general requirement for the PV modules and subsystems shall be the following

a.	Raw materials(solar Cells) and technology employed in the module production processes shall have to be certified and a certificate giving details of major materials i.e. cells, Glass, back sheet, their makes and data sheets to be submitted for the modules being supplied by the bidder.

b.	The rated output power of any supplied module shall have tolerance of +/- 3% as per MNRE standard specs.

c.	The peak-power point voltage and the peak-power point current of any supplied module and/or any module string (series connected modules) shall not  vary more than 2 (two) per cent from the respective arithmetic means for all  modules and/or for all module strings, as the case may be. The rated power of the module specified in “watt Peak” under STC may not have any negative tolerance.

d.	Except where specified, the front module surface shall consist of impact resistant, low-iron and high-transmission toughened glass.

e.	The module frame, if any, shall be made of a corrosion-resistant material which shall be electrolytically compatible with the structural material used for mounting the modules.

f.	The module shall be provided with a junction box with either provision of external screw terminal connection or sealed type and with arrangement for provision of by-pass diode. The box shall have hinged, weather proof lid with captive screws and cable gland entry points or may be of sealed type and IP65 rated.

g.	IV curves at STC and NOCT should be provided. The manufacturing process of the module and Major components of the module – solar cell, front glass, backsheet, encapsulant, sealant, their make and datasheet may be submitted by the bidder.

1.3	ARRAY STRUCTURE

1.3.1 Wherever required, suitable number of PV panel structures shall be provided. Structures shall be of flat-plate design either I or L sections.

1.3.2 Structural material shall be corrosion resistant and electrolytically compatible with the materials used  in  the  module  frame,  its  fasteners,  nuts  and  bolts. Galvanizing should meet ASTM A-123 hot dipped galvanizing or equivalent which provides at least spraying thickness of 70 microns on steel as per IS5905, if steel frame is used. Aluminium frame structures with adequate strength and in accordance with relevant latest BIS/ international standards can also be used.

1.3.3 Structures shall be supplied complete with all members to be compatible for allowing easy installation at the site.

1.3.4 The structures shall be designed to allow easy replacement of any module & can be either designed to transfer point loads on the roof top or UDL as per site conditions.

1.3.5 Each structure shall have a provision to adjust its angle of inclination to the horizontal as per the site conditions.

1.3.6 Each panel frame structure be so fabricated as to be fixed on the ground. The structure should be capable of withstanding a wind load of 200 km/hr after grouting & installation. The front end of the solar array must be one meter above the Ground. Grouting   material  for  SPV  structure  shall  be  as  per  M15  (1:2:4)  concrete specification.

1.3.7 The structures shall be designed for simple mechanical and electrical installation. There shall be no requirement of welding or complex machinery at the installation site. If prior civil work or support platform is absolutely essential to install the structures, the supplier shall clearly and unambiguously communicate such requirements along with their specifications in the bid. Detailed engineering drawings and instructions for such prior civil work shall be carried out prior to the supply of Goods.

1.3.8 The supplier shall specify installation details of the PV modules and the support structures with appropriate diagrams and  drawings  such  details  shall include, but not limited to, the following;

a.  Determination of true south at the site;

b.  Array tilt angle to the horizontal, with permitted tolerance;

c.  Details with drawings for fixing the modules;

d.  Details with drawings of fixing the junction/terminal boxes;

e.   Interconnection details inside the junction/terminal boxes;

f. Structure installation details and drawings;

g.  Electrical grounding (earthing);

h.  Inter-panel/Inter-row distances with allowed tolerances; and

i. Safety precautions to be taken.

The array structure shall support SPV modules at a given orientation and absorb and transfer the mechanical loads to the columns properly. All nuts and bolts shall be of very good quality stainless steel.

1.3.9 The design of mounting structures with fixed tilt shall be provided. The array structure shall be so designed that it occupies minimum space without sacrificing the output from SPV panels due to shadowing, orientation or tilt at the same time.

1.4 POWER CONDITIONING UNIT (PCU)

1.4.1 Power Conditioning Unit (PCU), grid interactive in nature, shall consist of MPPT controller, 10Nos inverters each of 10 KW rating, associated control and protection devices etc. all integrated into PCU. It shall provide necessary protections for Grid Synchronization and Data Logging/Monitoring. The PCU should convert DC power produced by SPV modules in to AC power and must synchronize automatically its AC output to the exact AC Voltage and frequency of Grid. The bidder may choose the inverter as string/Central as per their Design/ Project Philosophy.

Control Type:: Voltage source , microprocessor assisted , output regulation

Out put voltage			: 3 phase, 415 V ac (+5 %)

Frequency			: 50 Hz ( +3 Hz, -3 Hz)

Continuous rating			: 100 KVA Hybrid inverter (Grid tied and off Grid)

DC link voltage range 			: 0 to 600 V

Nominal Power			: 100 kVA

Standard conformation			: IEC 61683

Total Harmonic Distortion	: less than 3%

Operating temperature Range	: -250  to 600  C

Housing cabinet	: PCU to be housed in suitable switch cabinet, Within IP 20 degree of ingress protection

PCU efficiency	: 94 % and above at full load,

Power Control	: MPPT

1.4.2 The DC energy produced has to be utilized to maximum and supplied to the bus for inverting to AC voltage to extract maximum energy from solar array and provides 3-ph, 415V AC/ (+15% to – 10%), 50+/-1.5 Hz with total harmonic voltage distortion less than 3% to synchronize with local grid . DC voltage ripple content shall be not more than 3%.

1.4.3 The PCU shall be of very high quality having efficiency not less than 97% and shall be capable of running in integrated mode.

1.4.4 Degree of protection of the indoor PCU shall be at least IP-31and that of outdoor at least IP-55.

1.4.5 Built in with data logging to remotely monitor plant performance through external PC shall be provided (PC shall be provided along with SPV Plant).

1.4.6 The PCU shall be designed for continuous, reliable power supply as per specification.

1.4.7 The PCU should be designed to be completely compatible with the SPV array voltage and Grid supply voltage.

1.4.8 The dimension, weight, foundation details etc. of the PCU shall be clearly indicated in the detailed technical specification.

1.4.9 The system should be capable of providing all the data including that of meter and PCU to the central software on IEC-104 protocol. All the equipments /hardware /software for complying to the same will be in the bidder‟s scope.

1.4.10 The PCU shall be capable of complete automatic operation, including wake-up, synchronization & shut down independently& automatically.

1.4.11 Both AC & DC lines shall have suitable fuses, Metal Oxide Arrestors/surge arrestors and contactors to allow safe start up and shut down of the system. Fuses used in the DC circuit should be DC rated.

1.4.12 PCU shall operate in sleeping mode when there will no power connected.

1.4.13 Protections:

- Over voltage both at input & output.

- Over current both at input & output.

- Over/under grid frequency.

- Heat sink over temperature.

- Short circuit.

- Protection against lightening.

- Surge arrestors to protect against Surge voltage induced at output due to external source.

- Anti- Islanding Protection

1.4.14 It should have user friendly 4X40 LED/LCD display for programming and view on line parameters such as:

- Inverter per phase Voltage, current, kW, kVA and frequency,

- Grid Voltage and frequency,

- Inverter (Grid) on Line status,

- PV panel voltage,

- Solar charge current and ambient temperature,

- Individual power stage heat sink and cabinet temperature,

- Solar Radiation (with external pyranometer with in scope)

- Inverter Import export kWh summation

- Solar kWh summation

- Inverter on

- Grid on

- Inverter under voltage/over voltage

- Inverter over load

- Inverter over temperature.

1.4.15 The PCU shall have arrangement for adjusting DC input current and should trip against sustainable fault downstream and shall not start till the fault is rectified.

1.4.16 The 3 phase PCU shall be from internationally reputed firms, which will incorporate latest Technological advance to provide highly reliable and efficient energy conversion from DC to AC.

1.4.17 PCU shall be capable to synchronize independently & automatically with Discom grid power line frequency to attain synchronization and export power generated by solar plant to grid.

1.4.18 The PCU shall be capable of complete automatic operation, including wake-up, synchronization & shut down.

1.4.19 Typical failure analysis report of PCUs and recommended list of critical components shall be provided by the bidder while submitting their offer.

1.4.20 The PCU shall be capable of operating in parallel with the grid utility service and shall be capable of interrupting line fault currents and line to ground fault currents.

1.4.21 The PCU shall be able to withstand an unbalanced load conforming to IEC standard and relevant Indian electricity condition. The PCU shall include appropriate self-protective and self-diagnostic features to protect itself and the PV array from damage in the event of PCU component failure or from parameters – beyond the PCU‟s safe operating range due to internal or external causes. The self-protective features shall not allow signals from the PCU front panel to cause the PCU to be operated in a manner which may be unsafe or damaging. Faults due to malfunctioning within the PCU, including commutation feature, shall be cleared by the PCU protective devices and not by the existing site utility grid service circuit breaker.

1.4.22 The PCU shall go to shutdown/standby mode, with its contacts open, under the following conditions before attempting an automatic restart after an appropriate time delay.

 When the power available from the PV array is insufficient to supply the losses of the PCU, the PCU shall go to standby/shutdown mode.

 The PCU control shall prevent excessive cycling of shut down during insufficient solar radiance.

1.4.23 Operation outside the limits of power quality as described in the technical data sheet should cause the power conditioner to disconnect the grid. Additional parameters requiring automatic disconnection are

i. Neutral voltage displacement

ii. Over current

iii. Earth fault

iv. And reverse power

In each of the above cases, tripping time should be very less.

1.4.24 Detailed technical description of the complete unit of offered PCU should be furnished with bid document Following Technical documents of PCU shall be supplied for approval after placement of order.

 Detailed technical description of the complete unit

 Instructions for installation and operation

 Electrical diagrams of all internal cabling, necessary for installation, maintenance and fault finding.

 Description of electrical and mechanical characteristics of units.

 Maintenance and fault finding procedures.

 Safety precautions.

 Software for data monitoring with detailed description.

 Details of data acquisition

 Details of Telemetry linking

 Factory test reports in details on various parameters.

 Trouble shooting procedures.

 All maintenance requirements and their schedules, including detailed instructions on how to perform each task.

 Detailed schematics of all power instrumentation and control equipment and subsystems along with their interconnection diagrams. Schematics shall indicate wiring diagrams, their numbers and quantities, type and ratings of alt components and subsystems.

 A detailed bill of materials which shall list components model numbers, quantities and manufacturer of each supplied item.

 All documents and write ups shall be in English. They shall be clean and legible, and must be checked, signed, approved and dated by a competent representative of the contractor.

1.4.25 The Bidder should note that PCU will be installed in Tirupati which is hot place and prone to dust, hot air of 52 degree centigrade. Thus the room shelter, air blower/ fan (auto operated as per requirement) if required, for PCU will be in scope of supply. Preference should be given to PCU which does not require such protection being desert with extreme climatic conditions

1.4.26 The Bidder shall provide data sheet for Power Conditioning Unit along with their offer as per Guaranteed Technical Particular

1.4.27 Communication Modbus protocol with LAN/WAN options along with remote access facility and SCADA package with latest monitoring systems

1.4.28 Electrical safety, earthing and protection

a.	Internal Faults: In built protection for internal faults including excess temperature, commutation failure, overload and cooling fan failure (if fitted) is obligatory.

b.	Galvanic Isolation: Galvanic Isolation is required to avoid any DC component being injected into the grid and the potential for AC components appearing at the array.

c. Over Voltage Protection: Over Voltage Protection against atmospheric lightning discharge to the PV array is required. Protection is to be provided against  voltage fluctuations in the grid itself and internal faults in the power conditioner, operational errors and switching transients.

d. Earth fault supervision: An integrated earth fault device shall have to be provided to detect eventual earth fault on DC side and shall send message to the supervisory system.

e. Cabling practice: Cable connections must be made using PVC Cu cables,  as per BIS  standards. All cable connections must  be made using suitable terminations for effective contact. The PVC Cu cables must be run in GL trays with covers for protection.

f. Fast acting semiconductor type current limiting fuses at the main bus- bar to protect from the grid short circuit contribution.

1.4.29 The PCU shall include an easily accessible emergency OFF button located at an appropriate position on the unit.

1.4.30 The PCU shall include ground lugs for equipment and PV array grounding.

1.4.31  All exposed surfaces of ferrous parts shall be thoroughly cleaned, primed, and  painted or otherwise suitably protected to survive a nominal 30 years design life of the unit.

1.4.32  The PCU enclosure shall be weatherproof and capable of surviving climatic changes  and should keep the PCU intact under all conditions in the room where it will be housed. The inverter shall be located indoor and should be either wall / pad mounted. Moisture condensation and entry of rodents and insects shall be prevented in the PCU enclosure.

1.4.33  Components and  circuit  boards mounted inside  the  enclosures shall  be clearly identified with appropriate permanent designations, which shall also serve to identify the items on the supplied drawings.

1.4.34  All doors, covers, panels and cable exits shall be gasketed or otherwise designed to limit the entry of dust and moisture. All doors shall be equipped with locks. All openings shall be provided with grills or screens with openings no larger than 0.95 cm. (about 3x8 inch).

1.4.35  In the design and fabrication of the PCU the site temperature ( 5° to 55°C), incident  sunlight and the effect of ambient temperature on component life shall be considered carefully. Similar consideration shall be given to the heat sinking and thermal for blocking diodes and similar components.

1.5  Factory Testing:

a. The PCU shall be tested to demonstrate operation of its control system and the  ability to be automatically synchronized and connected in parallel with a utility service, prior to its shipment.

b. Operation of  all  controls, protective  and  instrumentation  circuits  shall  be demonstrated by direct test if feasible or by simulation operation conditions for all parameters that can not be directly tested.

c. Special attention shall be given to demonstration of utility service interface protection circuits and functions, including calibration and functional trip tests of faults and isolation protection equipment.

d. Operation of start up, disconnect and shutdown controls shall also be tested and demonstrate. Stable operation of the PCU and response to control signals shall also be tested and demonstrated.

e. Factory testing shall not only be limited to measurement of phase currents, efficiencies,  harmonic content and power factor, but shall also include all other necessary tests/simulation required and requested by the Purchasers Engineers. Tests may be performed at 25,50,75 and 100 percent of the rated nominal power.

f. A factory Test Report (FTR) shall be supplied with the unit after all tests. The FTR   shall  include  detailed  description  of  all  parameters  tested  qualified  and warranted.'   A  blank format of FTR along with details of test to be conducted be provided along with the bid.

g. Factory testing of the PCU/ PCU,s should be carried out and witnessed by the Purchaser's Engineers at the manufacturers premises.

1.6  PLANT METERING/DATA LOGGING

a) PV array energy production :  Digital Meters to log the actual value of AC/DC Voltage, Current & Energy generated by the PV system shall have to be  provided. Two way  LT 415V energy meter (Import -  Export metering) shall be incorporated in the system on the main LT AC Grid supply.

b) Solar Irradiance an integrating pyranometer (Class II or better) should be provided  with the sensor mounted in the plane of the array. Readout should be integrated with data logging system.

c) Wind Speed : An integrated wind speed measurement unit be provided.

d) Temperature Sensor: Integrated temp, sensors for measuring the module surface  temp., invertor inside enclosure temp, and ambient temp to be provided complete with readouts integrated with the data logging system.

e) GSM Modem / Wi Fi modem in case GSM connectivity is used or Wireless Router + modem in case Ethernet connection is being used for remote access must be provided.

f) Remote Supervisory Control and data acquisition through SCADA software at the  purchasers  location  with  latest  software/hardware configuration  and  service connectivity for online / real time data monitoring/control complete to be supplied and operation and maintenance/control to be ensured by the supplier.

All major parameters should be available on the digital bus and logging facility for energy auditing through the internal microprocessor and can be read on the digital front panel at any time the current values, previous values for up to a month and the average values. The following parameters should be accessible via the operating interface display and also on the dedicated laptop in the office of the CMD/APSPDCL and the CGM/Projects through internet.

AC Voltage

AC Output current

Output Power

DC Input Voltage

DC Input Current

Time Active

Time disabled

Time Idle

Temperatures (C)

Invertors Status

Module temperature

Protective function  limits  (Viz  –  AC  overload  voltage,  AC  under  voltage,  Over frequency. Under frequency, ground fault. PV starting voltage, PV stopping voltage, Over  voltage delay, Under voltage delay, over frequency, Ground fault delay, PV starting delay, PV stopping delay).

1.70 PCU/ARRAY SIZE RATIO

The PCU continuous power rating shall be above 94% at full load.

1.8 PCU

Technical data sheet:-

The PCU	shall	continuously and	control the	utility interface within	the

stipulated range:-

On three Phase side:-

Output voltage	415(+5%) VAC

Frequency	50HZ(+3 HZ, -3 HZ)

Maximum current ripple	3% PP

Reactive Power	0.95 inductive to 0.95 capacitive

1.9 MAXIMUM POWER POINT TRACKER (MPPT)

Maximum power point tracker shall be integrated in the PCU to maximize energy  drawn  from  the  array.  The  MPPT  should  be  micro  processor based  to minimize  power  losses.  The  details  of  working  mechanism  of  MPPT  shall  be mentioned. The MPPT  must have provision (.manual setting) for constant voltage operation.

The Charge Controller should be capable of working on MPPT charging of the battery bank from SPV array and hybrid SPV/grid charging. The hybrid charging mode may give priority to SPV.

The charge controller must incorporate algorithms for efficient charging such as  MPPT, PWM, charge equalization etc. Details about these algorithms may be given  with  the  data sheet. The system must have very high power conversion efficiency.

The charge controller may have high input power factor. The THD of current drawn should be less than 5% and shall be specified.

The charge controller shall incorporate all necessary protections, including input  side protection etc. All aspects such as Depth of Discharge, etc. shall be verifiable.

The charge controller must conform to IEC 62093.

1.10 (a) DISCONNECTION AND ISLANDING (GRID TIED MODE)

Disconnection of the PV generator in the event of loss of the main grid supply while on Grid Tied Mode (on Saturday, Sunday and holidays where generated power is to be evacuated to Sub-Station-I) is to be achieved by in built protection within the power  conditioner. this may be achieved through rate of change of current, phase angle, unbalanced voltage or reactive load variants.

Operation outside the limits of power quality as described in the technical data   sheet  should  cause  the  power  conditioner  to  disconnect  from  the  grid. Additional   parameters  requiring  automatic  disconnection  are:  Neutral  voltage displacement, Over  current, Earth fault and reverse power.   In case of the above cases, tripping time should be less than (15 seconds).  Response time in case of grid failure due to switch off or failure based shut down should be well within 5 seconds. In case of use of two PCUs, the capacity of suitable equipment for synchronising with the AC out put of both the PCUs to the ACDB / Grid should be provided.

1.11 (b) DISCONNECTION (OFF GRID TIED MODE)

Since,  the  PCU  from  the  ACDB  is  required  to  supply  power  at  five aforementioned  different  places,  any  over  lover  load  detected  at  PCU,  should intelligently actuate changeover switch at any one place aforementioned above to bring the  connected load within the available capacity of SPV generation within 5 seconds  to  ensure  continued  utilization of  generated  energy. The  changeover switches  should  be  automatic  and  should  have  double  throw,  so  that  the disconnected load from SPV generation can be connected to grid automatically. And, on availability of appropriate generation capacity be reconnected.  In case of any unbalance  detected at ACDB appropriate measures like, phase swapping of conductors feeding passive off grid loads to reduce the unbalance within 30%.  Only in case of single phasing or unbalance beyond the scope after phase swapping of more than 30% the disconnection be made within 15 seconds.

1.12  AUTOMATIC RECONNECTION	AFTER	THE	GRID	FAILURE	IS RESTORED

PCU shall have the facility to automatically reconnect the PCU to the grid following restoration of grid subsequent to grid failure condition.  The PCU should wait for 5 seconds to attempt reconnection.

1.13 ARRAY JUNCTION BOX, MAIN JUNCTION BOXES :

The junction boxes are to be provided in the PV yard for termination of connecting cables. The J. Boxes shall be made of FRP/Powder Coated Aluminium with  full   dust,  water  &  vermin  proof  arrangement.  All  wires/cables  must  be terminated   through  cable  lugs.  The  J.Bs  shall  be  such  that  input  &  output termination can be made through suitable cable glands.

Made of FRP or cast aluminium/ copper

Copper  bus  bars/terminal  blocks  housed  in  the junction	box with suitable termination threads

Conforming to IP65 standards and IEC 62208 Hinged door with EPDM rubber gasket to prevent water entry. Single compression cable glands. Provision of earthing. it should be placed at 5 feet height or above for ease of accessibility.

Each Junction Box shall have High quality Suitable capacity Metal Oxide Varistors(MOVs) / surge arrestors, suitable Reverse Blocking Diodes. The  Junction Boxes shall have suitable arrangement monitoring and disconnection for each of the groups.

1.14	PLANT CONTROL, DATA LOGGER & PLANT MONITORING UNIT

Basically, this unit should perform the following .

•	Measurement and/or recording of energy parameters.

•	Simple data logger or energy meter to record the energy data on a pre determined interval basis.

•	Measurement &  continuous acquisition of  ambient  air  temperature, wind speed,  solar radiation, PV module temperature, PCU output voltage and current, output frequency, currents in the cables at aforementioned locations at the receiving ends.

•	Operating state monitoring and failure indication.

•	Representation of monitored data in graphics mode or in tabulation  mode.

•	Controlling & monitoring the entire power system through remote terminal.

•	Necessary hardwares & softwares shall have to be supplied by the bidder.

Both the softwares and hardwares required for interfacing the plant with office including CPUs, modems UPS are to be supplied and installed by the contractor.

•	Remote control/  Instrumentation:  The  microprocessor control  unit  should have the provision for installation of RS – 232/485 communication link.

1.15	DC DISTRIBUTION BOARD

DC distribution board shall be provided in between solar array and PCU. It shall have MCCB of suitable rating for connection and disconnection of array section. It shall have meters for measuring the array voltage and array current. DCDB can also be integrated into PCU for space saving.

DC DPBs shall have sheet from enclosure of dust & vermin proof. The bus bars are to made of copper of desired size. Suitable capacity MCBs be provided for controlling the DC power output to the PCU along with necessary surge arrestors.

1.16	AC DISTRIBUTION PANEL BOARD

1.16.1 Power conditioning unit installed in a control room converts DC energy produced by the solar array to AC energy. The AC power output of the inverter shall be fed to the ACDB (metering panel & isolation panel) which also houses energy meter. The 415V AC output of the isolation panel shall be fed to the grid. AC energy is then synchronized with the grid and power is consumed by load or may export to the grid.

1.16.2. ACDB shall be floor mounted type and shall have all the measuring instruments such as voltmeter, ammeter, frequency meter, Energy Meter {for measuring the deliverable units {kWh} for sale, selector switches and Mimic panel.

1.16.3. All the power cables shall be taken through top/ Bottom of the panel as per site requirement.

1.16.4. The ACDB shall fitted with suitable rating & size copper bus, MCCB, HRC fuses/circuit breaker/isolator, indicators for all incomer and outgoing terminals, LED voltmeter & Ammeter with suitable selector switches to monitor & measure the power to be evacuated.

1.16.5. Nut & bolts including metallic shall have to be adequately protected against atmosphere and weather prevailing in the area.

1.16.6. The overall dimension, weight, sheet thickness, painting etc. should be indicated by the Contractor.

1.16.7 The ACDB must carryout phase swapping of conductors feeding passive off grid load to different aforementioned locations  to reduce unbalance within 30%.

1.16.8 All switches and the circuit breakers, connectors should confirm to IEC 60947, part I, II and III.

1.16.9	The change over switches, cabling work should be undertaken by the bidder as part of the project.

1.17	CABLES & WIRES

1.17.1	Cabling in the yard and control room : Cabling in the yard shall be carried  out as per IE Rules. All other cabling above ground should be suitably mounted on cable trays with proper covers.

1.17.2	Wires: Only FRLS copper wires of appropriate size and of reputed make shall have to be used.

1.17.3	Cables  Ends:  All  connections  are  to  be  made  through  suitable cable/lug/terminals; crimped properly & with use of Cable Glands.

1.17.4	Cable Marking: All cable/wires are to be marked in proper manner by good quality ferule or by other means so that the cable can be easily identified.

Any  change  in  cabling  schedule/sizes  if  desired  by  the  bidder/supplier  be  got approved after citing appropriate reasons, All cable schedules/layout drawings have to  be  got  approved from ‘he purchaser prior to installation. All cable tests and measurement methods should confirm to IEC 60189.

1.18 Cable specifications:

• Multi strand, annealed high conductivity copper conductor

• PVC type ‘A’ pressure extruded insulation

• Overall PVC insulation for UV protection and confirm to IEC 69947

• Armoured cable for under ground laying

• All cables shall conform to BiS standards (IS 694) and (IS 1554)

• The size of each type of cable selected shall be based on minimum voltage drop, however, the maximum drop shall be limited to 3%

• Selected cable should carry a current density of minimum 1.2Amp/Sq.mm

• All electrical cables / wires inside the building to be fixed in accordance with specifications for electrical works.

• Proper laying of cables have to be ensured in appropriate cable trays, pipes /

trenches as per site requirement.

• A.C. supply cables to be terminated at the DB / LT bus bar.

• For laying / termination of cables, latest BIS / lEC codes / standards be followed.

1.19	FIRE EXTINGUISHERS:

The fire fighting system for the proposed power plant for fire protection shall be consisting of:

•	Portable fire extinguishers in the control room for fire caused by electrical short circuits.

•	Sand buckets in the control room

The installation of Fire Extinguishers should confirm to TAC regulations and BIS standards. The fire extinguishers shall be provided in the control room housing the batteries and PCUs as well as on the site where the PV arrays have been installed.

1.20	LIGHTNING PROTECTION:

There shall be the required number of suitable lightning arrestors installed in the  array field. Lightning protection shall be provided by the use of metal oxide varistors or  lightening arrestors and suitable earthing such that induced transients find an alternate route to earth. Protection shall meet the safety rules as per Indian Electricity Act. The Lightning conductor shall be earthed through flats and connected to earth pits as per applicable Indian Standards. Each Lightning conductor shall be fitted with individual earth pit as required.

1.21	EARTHING PROTECTION

Each array structure of the PV yard should be grounded properly. The array structures shall be connected to earth pits as per IS Standards.	In addition the lightning arrester/masts should also be provided inside the array field. Provision should  be kept be provided inside the array field. Provision should be kept for shorting and grounding of the PV array at the time of maintenance work. All metal casing/shielding of  the plant should be thoroughly grounded in accordance with Indian electricity Act./IE  Rules.  Earth resistance should be tested in presence of the representative of APSPDCL after earthing by calibrated earth tester. PCU ACDB & DCDB should be earthed properly.

1.22	TOOLS & TACKLES AND SPARES:

After  completion  of  installation  &  commissioning  of  the  power  plant, necessary  tools  &  tackles  are  to  be  provided  free  of  cost  by  the  bidder  for maintenance purpose. List of tools and tackles to be supplied by the bidder for approval of specifications and make from APSPDCL.

A list of requisite spares in case of PCU comprising of a set of control logic cards, IGBT driver cards etc. Junction Boxes. Fuses, MOVs / arrestors, MCCBs etc along with  spare set of PV modules and batteries be indicated, which shall be supplied along with the equipment. A minimum set of spares (5%) shall be maintained in the plant itself for the entire period of warranty and Operation & Maintenance which upon its use shall be replenished.

1.23	DANGER BOARDS AND SIGNAGES

Danger boards should be provided as and where necessary as per IE Act./IE

rules as amended up to date. Three signages shall be provided one each at battery

–cum- control room, solar array area and main entry from administrative block. Text of the signages may be finalised in consultation with APSPDCL.

1.24	DRAWINGS & MANUALS

Two copies of Engineering, electrical drawings and Installation and O&M manuals are to be supplied. Bidders shall provide complete technical data sheets for each equipment giving details of the specifications along with make/makes in their bid	along	with	basic	design	of	the	power	plant	and	power	evacuation, synchronization and distribution for lighting system along with protection equipment. Approved ISI and reputed makes for equipment be used.

For  complete  electro-mechanical  works,  bidders  shall  supply  complete design,  details  and  drawings  for  approval  to  APSPDCL  before  progressing  with  the installation work

FORMS OF SECURITIES

FORMS OF SECURITIES

Acceptable forms of securities are annexed.  Bidders should not complete the Performance Security forms at this time.  Only the successful Bidder will be required to provide Performance Security in accordance with one of the forms, or in a similar; for acceptable to the Employer.

Annex A :	Performance Bank Guarantee

ANNEXURE-A

#### PERFORMANCE BANK GUARANTEE

## BANK GUARANTEE

This Guarantee made on this __________ day of __________ 2013 between __________ Bank Limited, a Company incorporated in __________ having its registered office at __________ and one of its branch office at __________ Mumbai __________ hereinafter called the "Bank" which expression shall unless repugnant to the context or contrary to the meaning thereof shall include its successors and assigns) of the One Part and ___________________________, a Company incorporated in India under the Companies Act, 1956 and having its registered office at ________________________(hereinafter called " Purchaser" which expression shall include its successors) of the Other Part.

WHEREAS

- The Supplier has entered in to an agreement with the purchaser (Contract No. _______ dated___________ for supply of _________________ herein after called ‘’the Contract”.

- As per the terms of the Contract the Supplier has to provide a Bank Guarantee from a *Nationalized Bank for an amount of Rs____________*(the “Guaranteed Amount”) for the due performance of the Suppliers Obligations in accordance with the Contract in favour of the Purchaser. A copy of the Contract is enclosed with this Bank Guarantee.

- The Bank has, at the request of Supplier, agreed to give in favour of the Purchaser a Guarantee for payment of the Guaranteed Amount in a manner hereinafter appearing which the Purchase has agreed to accept.

NOW THIS DEED WITNESSETH AS FOLLOWS:

- In pursuance of the said Contract and in consideration of the premises, the Bank hereby unconditionally and irrevocably, and without any qualification whatsoever, agrees, covenants, undertakes and guarantees, as primary obligator and not as surety merely, to make payment to Purchaser on its first demand without whatsoever any claims, objection, protest or demur and without any recourse to the Supplier, notwithstanding any intimation or direction to the contrary or any objection, such sum or sums of money to the extent of and upto the Guaranteed Amount up to and including 14*days after the due performance of the suppliers obligation including any warranty and FMS obligations and termination of the said Contract

- Any such demand placed on the Bank shall be conclusive as regards the Guaranteed Amount due and payable by the Bank under this Guarantee.

- This Guarantee is executed up to and including a period of _14__days after the due performance of the supplier’s obligation and termination of the said Contract during which period it is not revocable except with the previous written consent of Purchaser.

- Purchaser may, without affecting Bank’s liabilities and obligations hereunder, grant time or other indulgence to or compound with Supplies or enter into any agreement or agree to forbear to enforce any of the terms and conditions of this Guarantee.

- This Guarantee shall not be affected by any change in the constitution of Purchaser or Supplier by merger, amalgamation or absorption with any other body or corporation or otherwise and this Guarantee will be available to or enforceable by or against such body or corporation.

In order to give effect to this Guarantee, Purchase shall be entitled to act as if the Bank were the principal debtor and the Bank hereby waives all and any of its rights of surety ship.

Any notice by way of request and demand or otherwise hereunder sent by telex, fax or personally served, or by registered post addressed as aforesaid to the Bank in Mumbai, India shall be presumed to have been duly received by the Bank as follows:

(i)	If personally served, when served.

(ii)	If by fax or telex on the second business day after the transmission.

(iii)	If mailed, upon receipt, or on seventh day after deposit in the mail with postage prepaid. The Guarantee herein contained is not revocable by notice during its currency and shall remain in full force until payment has been made to Purchase by Bank of the Guaranteed Amount payable hereunder.

The liability of the Bank is irrevocable during the currency of this Bank Guarantee and is restricted to the Guaranteed Amount viz. Rs ____________(Rupees ________________Only).

Unless demand or claim under this Guarantee is received by the Bank in writing within the validity period of this Guarantee, all the rights of Purchase against the Bank shall be forfeited and the Bank shall be relieved and discharged of all liabilities hereunder.

These Presents shall be governed by and construed in accordance with the Indian Law, and the courts in ________alone shall have exclusive jurisdiction in relation hereto.

The Bank hereby declares that it has power to issue this Guarantee and the undersigned have the full power to approve execution, delivery and the performance of the Guarantee.

Signed, sealed and delivered by the Bank

For _____________________

Authorized Signatories